## Conductors - AL
Code | AWG | Aluminum/ Steel | Resistance- dc 20 °C (Ω/kft) | Resistance- ac 25 °C (Ω/kft) | Resistance- ac 75 °C (Ω/kft) | Reactance Capacitive (MΩ/kft) | Reactance Inductive (Ω/kft) | GMR -ft | Ampacity (amps) | Type | Conductor Diameter (in) | Steel Core (Inches) | Nominal Mass (lb/kft) | Aluminum (lb/kft) | Steel Core (lb/kft) | Rated Strength (lb)
| 18 | 1 | 8.264 |  | 10.33 |  |  | 0.0013077 | 4.4 | SOLID_AL | 0.0403
| 17 | 1 | 6.5424 |  | 8.178 |  |  | 0.00147 | 6.16 | SOLID_AL | 0.0453
| 16 | 1 | 5.2024 |  | 6.503 |  |  | 0.0016485 | 8.8 | SOLID_AL | 0.0508
| 15 | 1 | 4.1176 |  | 5.147 |  |  | 0.0018529 | 13.2 | SOLID_AL | 0.0571
| 14 | 1 | 3.2672 |  | 4.084 |  |  | 0.00208 | 17.6 | SOLID_AL | 0.0641
| 13 | 1 | 2.5896 |  | 3.237 |  |  | 0.0023364 | 26.4 | SOLID_AL | 0.072
| 12 | 1 | 2.0568 |  | 2.571 |  |  | 0.002622 | 35.2 | SOLID_AL | 0.0808
| 11 | 1 | 1.632 |  | 2.040 |  |  | 0.0029432 | 51.04 | SOLID_AL | 0.0907
| 10 | 1 | 1.2928 |  | 1.616 |  |  | 0.0032775 | 66 | SOLID_AL | 0.101
| 9 | 1 | 1.0256 |  | 1.282 |  |  | 0.0036993 | 70.4 | SOLID_AL | 0.114
| 8 | 1 | 0.8128 |  | 1.016 |  |  | 0.0041536 | 79.2 | SOLID_AL | 0.128
| 7 | 1 | 0.6448 |  | 0.806 |  |  | 0.0046728 | 96.8 | SOLID_AL | 0.144
Turkey | 6 | 6/1 | 0.6448 |  | 0.806 |  |  | 0.00394 | 105 | ACSR | 0.198 | 0.0661 | 36 | 24.5 | 11.6 | 1,190
| 5 | 1 | 0.40576 |  | 0.5072 |  |  | 0.0058734 | 123.2 | SOLID_AL | 0.181
Swan | 4 | 6/1 | 0.4030 |  | 0.515 |  |  | 0.00437 | 140 | ACSR | 0.250 | 0.0834 | 57 | 39.0 | 18.4 | 1,860
Swanate | 4 | 7/1 | 0.3990 |  | 0.519 |  |  | 0.00452 | 140 | ACSR | 0.257 | 0.1029 | 67 | 39.0 | 28.0 | 2,360
Sparrow | 2 | 6/1 | 0.2540 |  | 0.332 |  |  | 0.00418 | 184 | ACSR | 0.316 | 0.1052 | 91 | 62.0 | 29.3 | 2,850
Sparate | 2 | 7/1 | 0.2510 |  | 0.338 |  |  | 0.00504 | 184 | ACSR | 0.325 | 0.1299 | 107 | 62.0 | 44.7 | 3,640
Robin | 1 | 6/1 | 0.2010 |  | 0.268 |  |  | 0.00418 | 212 | ACSR | 0.354 | 0.1181 | 115 | 78.2 | 36.9 | 3,550
Raven | 1/0 | 6/1 | 0.1590 |  | 0.217 |  |  | 0.00446 | 242 | ACSR | 0.398 | 0.1327 | 145 | 98.7 | 46.6 | 4,380
Quail | 2/0 | 6/1 | 0.1260 |  | 0.176 |  |  | 0.0051 | 276 | ACSR | 0.447 | 0.1489 | 183 | 124.3 | 58.7 | 5,300
Pigeon | 3/0 | 6/1 | 0.1000 |  | 0.144 |  |  | 0.006 | 315 | ACSR | 0.502 | 0.1672 | 231 | 156.7 | 74.0 | 6,620
Penguin | 4/0 | 6/1 | 0.0795 |  | 0.119 |  |  | 0.00814 | 357 | ACSR | 0.563 | 0.1878 | 291 | 197.7 | 93.4 | 8,350
WAXWING | 266.8 | 18/1 | 0.0644 | 0.0657 | 0.0788 | 0.576 | 0.0934 | 0.0197 | 449 | ACSR | 0.609 | 0.1217 | 289.1 | 249.9 | 39.2 | 13.6
PARTRIDGE | 266.8 | 26/7 | 0.0637 | 0.0652 | 0.0778 | 0.565 | 0.0881 | 0.0217 | 475 | ACSR | 0.642 | 0.236 | 366.9 | 251.3 | 115.6 | 31.5
MERLIN | 336.4 | 18/1 | 0.0510 | 0.0523 | 0.0625 | 0.560 | 0.0877 | 0.0221 | 519 | ACSR | 0.684 | 0.1367 | 364.8 | 315.3 | 49.5 | 13.6
LINNET | 336.4 | 26/7 | 0.0506 | 0.0517 | 0.0619 | 0.549 | 0.0854 | 0.0244 | 535 | ACSR | 0.720 | 0.265 | 462.0 | 316.5 | 145.5 | 31.5
ORIOLE | 336.4 | 30/7 | 0.0502 | 0.0513 | 0.0614 | 0.544 | 0.0843 | 0.0255 | 529 | ACSR | 0.741 | 0.318 | 526.4 | 317.7 | 208.7 | 39.6
CHICKADEE | 397.5 | 18/1 | 0.0432 | 0.0443 | 0.0528 | 0.544 | 0.0856 | 0.0240 | 579 | ACSR | 0.743 | 0.1486 | 431.0 | 372.5 | 58.5 | 13.6
IBIS | 397.5 | 26/7 | 0.0428 | 0.0438 | 0.0525 | 0.539 | 0.0835 | 0.0265 | 587 | ACSR | 0.783 | 0.288 | 546.0 | 374.1 | 171.9 | 31.5
LARK | 397.5 | 30/7 | 0.0425 | 0.0434 | 0.0519 | 0.533 | 0.0824 | 0.0277 | 594 | ACSR | 0.806 | 0.345 | 621.8 | 375.2 | 246.6 | 39.6
PELICAN | 477.0 | 18/1. | 0.0360 | 0.0369 | 0.0441 | 0.528 | 0.0835 | 0.0263 | 646 | ACSR | 0.814 | 0.1628 | 517.3 | 447.1 | 70.2 | 13.6
FLICKER | 477.0 | 24/7 | 0.0358 | 0.0367 | 0.0439 | 0.524 | 0.0818 | 0.0283 | 655 | ACSR | 0.846 | 0.282 | 613.9 | 449.4 | 164.5 | 26.8
HAWK | 477.0 | 26/7 | 0.0357 | 0.0366 | 0.0438 | 0.522 | 0.0814 | 0.0290 | 659 | ACSR | 0.858 | 0.316 | 655.3 | 448.9 | 206.4 | 31.5
HEN | 477.0 | 30/7 | 0.0354 | 0.0362 | 0.0434 | 0.517 | 0.0803 | 0.0304 | 666 | ACSR | 0.883 | 0.378 | 746.4 | 450.4 | 296.0 | 39.6
OSPREY | 556.5 | 18/1 | 0.0309 | 0.0318 | 0.0379 | 0.518 | 0.0818 | 0.0284 | 711 | ACSR | 0.879 | 0.1758 | 603.3 | 521.4 | 81.9 | 13.6
PARAKEET | 556.5 | 24/7 | 0.0307 | 0.0314 | 0.0377 | 0.512 | 0.0801 | 0.0306 | 721 | ACSR | 0.914 | 0.304 | 716.1 | 524.3 | 191.8 | 26.8
DOVE | 556.5 | 26/7 | 0.0305 | 0.0314 | 0.0375 | 0.510 | 0.0795 | 0.0313 | 726 | ACSR | 0.927 | 0.341 | 765.2 | 524.2 | 241.0 | 31.5
EAGLE | 556.5 | 30/7 | 0.0300 | 0.0311 | 0.0371 | 0.505 | 0.0786 | 0.0328 | 734 | ACSR | 0.953 | 0.409 | 870.7 | 525.4 | 345.3 | 39.6
PEACOCK | 605.0 | 24/7 | 0.0282 | 0.0290 | 0.0347 | 0.505 | 0.0792 | 0.0319 | 760 | ACSR | 0.953 | 0.318 | 778.8 | 570.1 | 208.7 | 26.8
SWIFT | 636.0 | 36/1 | 0.0267 | 0.0281 | 0.0334 | 0.509 | 0.0806 | 0.0300 | 769 | ACSR | 0.930 | 0.1329 | 642.8 | 596.0 | 46.8 | 7.3
KINGBIRD | 636.0 | 18/1 | 0.0269 | 0.0278 | 0.0332 | 0.507 | 0.0805 | 0.0301 | 773 | ACSR | 0.940 | 0.1880 | 689.9 | 596.3 | 93.6 | 13.6
ROOK | 636.0 | 24/7 | 0.0268 | 0.0277 | 0.0330 | 0.502 | 0.0786 | 0.0327 | 784 | ACSR | 0.977 | 0.326 | 818.2 | 599.1 | 219.1 | 26.8
GROSBEAK | 636.0 | 26/7 | 0.0267 | 0.0275 | 0.0328 | 0.500 | 0.0780 | 0.0335 | 789 | ACSR | 0.990 | 0.365 | 874.2 | 599.0 | 275.2 | 31.5
EGRET | 636.0 | 30/19 | 0.0266 | 0.0273 | 0.0326 | 0.495 | 0.0769 | 0.0351 | 798 | ACSR | 1.019 | 0.437 | 987.2 | 600.5 | 386.7 | 39.2
FLAMINGO | 666.6 | 24/7 | 0.0256 | 0.0263 | 0.0314 | 0.498 | 0.0780 | 0.0335 | 807 | ACSR | 1.000 | 0.333 | 857.9 | 628.2 | 229.7 | 26.8
STARLING | 715.5 | 26/7 | 0.0238 | 0.0244 | 0.0292 | 0.490 | 0.0767 | 0.0355 | 849 | ACSR | 1.051 | 0.387 | 983.7 | 674.0 | 309.7 | 31.5
REDWING | 715.5 | 30/19 | 0.0236 | 0.0242 | 0.0290 | 0.486 | 0.0756 | 0.0372 | 859 | ACSR | 1.081 | 0.463 | 1109.3 | 675.3 | 434.0 | 39.2
COOT | 795.0 | 36/1 | 0.0217 | 0.0225 | 0.0268 | 0.492 | 0.0780 | 0.0335 | 894 | ACSR | 1.040 | 0.1486 | 803.6 | 745.1 | 58.5 | 7.3
TERN | 795.0 | 45/7 | 0.0216 | 0.0225 | 0.0267 | 0.488 | 0.0764 | 0.0352 | 887 | ACSR | 1.063 | 0.266 | 895 | 749 | 146 | 16.3
CUCKOO | 795.0 | 24/7 | 0.0215 | 0.0223 | 0.0266 | 0.484 | 0.0763 | 0.0361 | 901 | ACSR | 1.092 | 0.364 | 1023 | 749 | 274.0 | 26.8
CONDOR | 795.0 | 54/7 | 0.0215 | 0.0222 | 0.0265 | 0.484 | 0.0759 | 0.0368 | 889 | ACSR | 1.092 | 0.364 | 1022 | 748 | 274.0 | 26.8
DRAKE | 795.0 | 26/7 | 0.0214 | 0.0222 | 0.0263 | 0.482 | 0.0756 | 0.0375 | 907 | ACSR | 1.108 | 0.408 | 1093 | 749 | 344 | 31.5
MALLARD | 795.0 | 30/19 | 0.0213 | 0.0220 | 0.0261 | 0.477 | 0.0744 | 0.0392 | 918 | ACSR | 1.140 | 0.489 | 1233.9 | 750.7 | 483.2 | 39.2
RUDDY | 900.0 | 45/7 | 0.0191 | 0.0200 | 0.0237 | 0.479 | 0.0755 | 0.0374 | 958 | ACSR | 1.131 | 0.283 | 1013 | 848 | 165 | 16.3
CANARY | 900.0 | 54/7 | 0.0190 | 0.0197 | 0.0235 | 0.474 | 0.0744 | 0.0392 | 961 | ACSR | 1.162 | 0.387 | 1158 | 848 | 310 | 26.8
RAIL | 954.0 | 45/7 | 0.0180 | 0.0188 | 0.0223 | 0.474 | 0.0748 | 0.0385 | 993 | ACSR | 1.165 | 0.291 | 1075 | 899 | 176 | 16.3
ORTOLAN | 1033.5 | 45/7 | 0.0167 | 0.0175 | 0.0208 | 0.468 | 0.0739 | 0.0401 | 1043 | ACSR | 1.212 | 0.303 | 1163 | 973 | 190 | 16.3
CURLEW | 1033.5 | 54/7 | 0.0165 | 0.0172 | 0.0201 | 0.464 | 0.0729 | 0.0420 | 1047 | ACSR | 1.245 | 0.415 | 1329 | 973 | 356 | 26.8
BLUEJAY | 1113.0 | 45/7 | 0.0155 | 0.0163 | 0.0193 | 0.462 | 0.0731 | 0.0416 | 1092 | ACSR | 1.259 | 0.315 | 1254 | 1049 | 205 | 16.3
FINCH | 1113.0 | 54/19 | 0.0154 | 0.0161 | 0.0191 | 0.458 | 0.0702 | 0.0436 | 1093 | ACSR | 1.293 | 0.431 | 1430 | 1054 | 376 | 26.3
BUNTING | 1192.5 | 45/7 | 0.0144 | 0.0152 | 0.0181 | 0.456 | 0.0723 | 0.0431 | 1139 | ACSR | 1.302 | 0.326 | 1342 | 1123 | 219 | 16.3
GRACKLE | 1192.5 | 54/19 | 0.0144 | 0.0151 | 0.0179 | 0.452 | 0.0710 | 0.0451 | 1140 | ACSR | 1.338 | 0.446 | 1531 | 1128 | 403 | 26.3
BITTERN | 1272.0 | 45/7 | 0.0135 | 0.0144 | 0.0170 | 0.451 | 0.072 | 0.0445 | 1184 | ACSR | 1.345 | 0.336 | 1432 | 1198 | 234 | 16.3
PHEASANT | 1272.0 | 54/19 | 0.0135 | 0.0142 | 0.0169 | 0.447 | 0.070 | 0.0466 | 1187 | ACSR | 1.382 | 0.461 | 1634 | 1205 | 429 | 26.3
DIPPER | 1351.5 | 45/7 | 0.0127 | 0.0136 | 0.0161 | 0.447 | 0.071 | 0.0459 | 1229 | ACSR | 1.386 | 0.347 | 1521 | 1273 | 248 | 16.3
MARTIN | 1351.5 | 54/19 | 0.0127 | 0.0134 | 0.0159 | 0.442 | 0.070 | 0.0480 | 1232 | ACSR | 1.424 | 0.475 | 1735 | 1279 | 456 | 26.3
BOBOLINK | 1431.0 | 45/7 | 0.0120 | 0.0129 | 0.0152 | 0.442 | 0.070 | 0.0472 | 1272 | ACSR | 1.427 | 0.357 | 1611 | 1348 | 263 | 16.3
PLOVER | 1431.0 | 54/19 | 0.0120 | 0.0127 | 0.0151 | 0.438 | 0.069 | 0.0495 | 1275 | ACSR | 1.465 | 0.489 | 1838 | 1355 | 483 | 26.3
LAPWING | 1590.0 | 45/7 | 0.0108 | 0.0117 | 0.0138 | 0.434 | 0.069 | 0.0498 | 1354 | ACSR | 1.504 | 0.376 | 1790 | 1498 | 292 | 16.3
FALCON | 1590.0 | 54/19 | 0.0108 | 0.0116 | 0.0137 | 0.430 | 0.068 | 0.0521 | 1359 | ACSR | 1.545 | 0.515 | 2042 | 1505 | 537 | 26.3
CHUKAR | 1780.0 | 84/19 | 0.0097 | 0.0106 | 0.0125 | 0.424 | 0.067 | 0.0534 | 1453 | ACSR | 1.602 | 0.437 | 2072 | 1685 | 387 | 18.7
BLUEBIRD | 2156.0 | 84/19 | 0.0080 | 0.0090 | 0.0105 | 0.409 | 0.065 | 0.0588 | 1623 | ACSR | 1.762 | 0.481 | 2508 | 2040 | 468 | 18.7
KIWI | 2167.0 | 72/7 | 0.0080 | 0.0092 | 0.0106 | 0.411 | 0.068 | 0.0570 | 1607 | ACSR | 1.735 | 0.347 | 2301 | 2052 | 249 | 10.8
THRASHER | 2312.0 | 76/19 | 0.0075 | 0.0086 | 0.0100 | 0.405 | 0.065 | 0.0600 | 1673 | ACSR | 1.802 | 0.407 | 2523 | 2188 | 335 | 13.3
JOREA | 2515.0 | 76/19 | 0.0069 | 0.0081 | 0.0093 | 0.399 | 0.064 | 0.0621 | 1751 | ACSR | 1.88 | 0.425 | 2749 | 2383 | 366 | 13.3
Partridge/TW | 266.8 | 16 | 0.3356 |  | 0.077708 |  |  | 0.0788 | 449 | ACSR/TW | 0.595 | 0.2364 | 366 | 250 | 116 | 11200
Linnet/TW | 336.4 | 16 | 0.2662 |  | 0.061648 |  |  | 0.0885 | 519 | ACSR/TW | 0.667 | 0.2655 | 462 | 316 | 146 | 14000
Oriole/TW | 336.4 | 23 | 0.265 |  | 0.061345 |  |  | 0.1059 | 525 | ACSR/TW | 0.693 | 0.3177 | 526 | 317 | 209 | 17100
Merlin/TW | 336.4 | 6 | 0.2693 |  | 0.062462 |  |  | 0.1367 | 508 | ACSR/TW | 0.630 | 0.1367 | 365 | 315 | 50 | 8560
FLICKER/TW | 477.0 | 18/7 | 0.0356 | 0.0365 | 0.0438 | 0.5370 | 0.0841 | 0.0257 | 641 | ACSR/TW | 0.776 | 0.2820 | 612.8 | 448.4 | 164.4 | 17,200
HAWK/TW | 477.0 | 18/7 | 0.0356 | 0.0360 | 0.0436 | 0.5349 | 0.0835 | 0.0264 | 645 | ACSR/TW | 0.789 | 0.3159 | 655 | 448.7 | 206.3 | 19,400
PARAKEET/TW | 556.5 | 18/7 | 0.0305 | 0.0313 | 0.0375 | 0.5248 | 0.0824 | 0.0277 | 707 | ACSR/TW | 0.835 | 0.3045 | 714.9 | 523.2 | 191.7 | 20,000
DOVE/TW | 556.5 | 20/7 | 0.0305 | 0.0312 | 0.0374 | 0.5232 | 0.0817 | 0.0286 | 711 | ACSR/TW | 0.852 | 0.3414 | 764.5 | 523.5 | 241 | 22,600
ROOK/TW | 636.0 | 18/7 | 0.0267 | 0.0274 | 0.0329 | 0.5164 | 0.0809 | 0.0296 | 767 | ACSR/TW | 0.890 | 0.3255 | 816 | 597.9 | 219.1 | 22,900
GROSBEAK/TW | 636.0 | 20/7 | 0.0266 | 0.0273 | 0.0328 | 0.5127 | 0.0802 | 0.0305 | 772 | ACSR/TW | 0.908 | 0.3648 | 873.5 | 598.4 | 275.1 | 25,400
TERN/TW | 795.0 | 17/7 | 0.0215 | 0.0222 | 0.0266 | 0.5042 | 0.0797 | 0.0312 | 869 | ACSR/TW | 0.960 | 0.2658 | 892 | 745.9 | 146.1 | 21,000
PUFFIN/TW | 795.0 | 18/7 | 0.0214 | 0.0220 | 0.0264 | 0.5011 | 0.0789 | 0.0323 | 876 | ACSR/TW | 0.980 | 0.3324 | 975.3 | 746.9 | 228.4 | 25,900
CONDOR/TW | 795.0 | 20/7 | 0.0213 | 0.0219 | 0.0263 | 0.4990 | 0.0784 | 0.0331 | 880 | ACSR/TW | 0.993 | 0.3639 | 1021 | 747.2 | 273.8 | 28,200
DRAKE/TW | 795.0 | 20/7 | 0.0212 | 0.0219 | 0.0262 | 0.4963 | 0.0778 | 0.0339 | 886 | ACSR/TW | 1.010 | 0.4080 | 1092 | 747.8 | 344.2 | 31,800
PHOENIX/TW | 954.0 | 30/7 | 0.0181 | 0.0188 | 0.0224 | 0.4900 | 0.0775 | 0.0343 | 956 | ACSR/TW | 1.049 | 0.2511 | 1032 | 901.6 | 130.4 | 23,700
RAIL/TW | 954.0 | 32/7 | 0.0180 | 0.0187 | 0.0222 | 0.4884 | 0.0771 | 0.0349 | 960 | ACSR/TW | 1.061 | 0.2913 | 1075 | 900 | 175 | 25,900
CARDINAL/TW | 954.0 | 20/7 | 0.0178 | 0.0184 | 0.0220 | 0.4852 | 0.0763 | 0.0362 | 985 | ACSR/TW | 1.084 | 0.3987 | 1226 | 897.3 | 328.7 | 33,500
SNOWBIRD/TW | 1033.5 | 30/7 | 0.0166 | 0.0174 | 0.0207 | 0.4842 | 0.0767 | 0.0356 | 1004 | ACSR/TW | 1.089 | 0.2613 | 1115 | 973.8 | 141.2 | 25,700
ORTOLAN/TW | 1033.5 | 32/7 | 0.0166 | 0.0174 | 0.0207 | 0.4826 | 0.0762 | 0.0363 | 1008 | ACSR/TW | 1.102 | 0.3030 | 1165 | 975.2 | 189.8 | 28,100
CURLEW/TW | 1033.5 | 21/7 | 0.0165 | 0.0174 | 0.0203 | 0.4784 | 0.0754 | 0.0377 | 1035 | ACSR/TW | 1.129 | 0.4149 | 1327 | 971.1 | 355.9 | 36,300
AVOCET/TW | 1113.0 | 30/7 | 0.0155 | 0.0162 | 0.0193 | 0.4784 | 0.0758 | 0.0369 | 1050 | ACSR/TW | 1.129 | 0.2712 | 1201 | 1048.9 | 152.1 | 27,500
BLUEJAY/TW | 1113.0 | 33/7 | 0.0154 | 0.0162 | 0.0192 | 0.4768 | 0.0754 | 0.0376 | 1055 | ACSR/TW | 1.143 | 0.3147 | 1254 | 1049.2 | 204.8 | 30,300
FINCH/TW | 1113.0 | 38/19 | 0.0154 | 0.0161 | 0.0191 | 0.4704 | 0.0740 | 0.0399 | 1071 | ACSR/TW | 1.185 | 0.4310 | 1429 | 1052.6 | 376.4 | 39,100
OXBIRD/TW | 1192.5 | 30/7 | 0.0144 | 0.0151 | 0.0181 | 0.4730 | 0.0750 | 0.0382 | 1095 | ACSR/TW | 1.167 | 0.2808 | 1286 | 1123 | 163 | 29,500
BUNTING/TW | 1192.5 | 33/7 | 0.0143 | 0.0151 | 0.0180 | 0.4715 | 0.0746 | 0.0390 | 1100 | ACSR/TW | 1.181 | 0.3255 | 1343 | 1124 | 219 | 32,400
GRACKLE/TW | 1192.5 | 38/19 | 0.0143 | 0.0149 | 0.0179 | 0.4662 | 0.0733 | 0.0412 | 1117 | ACSR/TW | 1.225 | 0.4460 | 1530 | 1127 | 403 | 41,900
SCISSORTAIL/TW | 1272.0 | 30/7 | 0.0135 | 0.0142 | 0.0170 | 0.4689 | 0.0743 | 0.0394 | 1139 | ACSR/TW | 1.203 | 0.2901 | 1372 | 1198 | 174 | 31,400
BITTERN/TW | 1272.0 | 35/7 | 0.0135 | 0.0142 | 0.0170 | 0.4667 | 0.0738 | 0.0403 | 1145 | ACSR/TW | 1.220 | 0.3363 | 1433 | 1199 | 234 | 34,600
PHEASANT/TW | 1272.0 | 39/19 | 0.0134 | 0.0140 | 0.0168 | 0.4615 | 0.0725 | 0.0426 | 1162 | ACSR/TW | 1.264 | 0.4605 | 1632 | 1202 | 430 | 44,100
DIPPER/TW | 1351.5 | 35/7 | 0.0127 | 0.0134 | 0.0160 | 0.4615 | 0.0731 | 0.0415 | 1187 | ACSR/TW | 1.256 | 0.3465 | 1522 | 1274 | 248 | 36,700
MARTIN/TW | 1351.5 | 39/19 | 0.0126 | 0.0132 | 0.0158 | 0.4567 | 0.0714 | 0.0438 | 1205 | ACSR/TW | 1.300 | 0.4745 | 1734 | 1278 | 456 | 46,800
BOBOLINK/TW | 1431.0 | 36/7 | 0.0120 | 0.0128 | 0.0152 | 0.4578 | 0.0725 | 0.0427 | 1229 | ACSR/TW | 1.291 | 0.3567 | 1613 | 1350 | 263 | 38,900
PLOVER/TW | 1431.0 | 39/19 | 0.0120 | 0.0126 | 0.0150 | 0.4541 | 0.0712 | 0.0451 | 1248 | ACSR/TW | 1.337 | 0.4885 | 1836 | 1353 | 483 | 49,600
LAPWING/TW | 1590.0 | 36/7 | 0.0108 | 0.0116 | 0.0138 | 0.4493 | 0.0714 | 0.0449 | 1308 | ACSR/TW | 1.358 | 0.3759 | 1791 | 1499 | 292 | 42,200
FALCON/TW | 1590.0 | 42/19 | 0.0108 | 0.0115 | 0.0136 | 0.4441 | 0.0700 | 0.0476 | 1330 | ACSR/TW | 1.408 | 0.5150 | 2040 | 1503 | 537 | 55,100
CHUKAR/TW | 1780.0 | 37/19 | 0.0097 | 0.0105 | 0.0124 | 0.4393 | 0.0697 | 0.0482 | 1405 | ACSR/TW | 1.445 | 0.4370 | 2063 | 1676 | 387 | 50,700
BLUEBIRD/TW | 2156.0 | 64/19 | 0.0080 | 0.0089 | 0.0104 | 0.4229 | 0.0672 | 0.0538 | 1585 | ACSR/TW | 1.608 | 0.4805 | 2515 | 2047 | 468 | 61,100
MOHAWK/TW | 571.7 | 18/7 | 0.0297 | 0.0305 | 0.0365 | 0.5232 | 0.0821 | 0.0281 | 717 | ACSR/TW | 0.846 | 0.3090 | 734.7 | 537.3 | 197.4 | 20,600
CALUMET/TW | 565.3 | 20/7 | 0.0300 | 0.0308 | 0.0369 | 0.5217 | 0.0815 | 0.0288 | 717 | ACSR/TW | 0.858 | 0.3438 | 776 | 532 | 244 | 22,900
MYSTIC/TW | 666.6 | 20/7 | 0.0255 | 0.0262 | 0.0314 | 0.5122 | 0.0803 | 0.0304 | 790 | ACSR/TW | 0.913 | 0.3330 | 856.3 | 626.6 | 229.7 | 24,000
OSWEGO/TW | 664.8 | 20/7 | 0.0255 | 0.0262 | 0.0313 | 0.5090 | 0.0798 | 0.0310 | 793 | ACSR/TW | 0.927 | 0.3732 | 913.4 | 625.4 | 288 | 26,600
MAUMEE/TW | 768.2 | 20/7 | 0.0222 | 0.0228 | 0.0273 | 0.5011 | 0.0788 | 0.0325 | 862 | ACSR/TW | 0.977 | 0.3585 | 987.8 | 722.1 | 265.7 | 27,700
WABASH/TW | 762.8 | 20/7 | 0.0222 | 0.0229 | 0.0274 | 0.4994 | 0.0784 | 0.033 | 863 | ACSR/TW | 0.990 | 0.3993 | 1047 | 717 | 330 | 30,500
KETTLE/TW | 957.2 | 32/7 | 0.0180 | 0.0187 | 0.0224 | 0.4884 | 0.0770 | 0.035 | 962 | ACSR/TW | 1.060 | 0.2919 | 1079 | 902.8 | 176.2 | 26,000
FRASER/TW | 946.7 | 35/7 | 0.0181 | 0.0188 | 0.0225 | 0.4852 | 0.0765 | 0.0358 | 963 | ACSR/TW | 1.077 | 0.3462 | 1142 | 894 | 248 | 29,600
COLUMBIA/TW | 966.2 | 21/7 | 0.0177 | 0.0182 | 0.0218 | 0.4842 | 0.0761 | 0.0364 | 993 | ACSR/TW | 1.092 | 0.4014 | 1241 | 908 | 333 | 34,000
SUWANNEE/TW | 959.6 | 22/7 | 0.0177 | 0.0182 | 0.0218 | 0.4821 | 0.0756 | 0.0373 | 996 | ACSR/TW | 1.108 | 0.4479 | 1318 | 903 | 415 | 37,000
CHEYENNE/TW | 1168.1 | 30/7 | 0.0148 | 0.0155 | 0.0185 | 0.4757 | 0.0753 | 0.0378 | 1081 | ACSR/TW | 1.155 | 0.2778 | 1260 | 1100.4 | 159.6 | 28,900
GENESSEE/TW | 1158.0 | 33/7 | 0.0149 | 0.0156 | 0.0186 | 0.4736 | 0.0749 | 0.0384 | 1081 | ACSR/TW | 1.165 | 0.3234 | 1308 | 1092 | 216 | 31,600
HUDSON/TW | 1158.4 | 25/7 | 0.0147 | 0.0152 | 0.0182 | 0.4694 | 0.0740 | 0.04 | 1111 | ACSR/TW | 1.196 | 0.4401 | 1489 | 1089 | 400 | 39,600
CATAWBA/TW | 1272.0 | 30/7 | 0.0136 | 0.0143 | 0.0170 | 0.4694 | 0.0743 | 0.0394 | 1139 | ACSR/TW | 1.203 | 0.2901 | 1372 | 1198 | 174 | 31,400
NELSON/TW | 1257.1 | 35/7 | 0.0137 | 0.0144 | 0.0172 | 0.4678 | 0.0740 | 0.04 | 1137 | ACSR/TW | 1.213 | 0.3345 | 1417 | 1185.7 | 231.3 | 34,200
YUKON/TW | 1233.6 | 38/19 | 0.0139 | 0.0145 | 0.0173 | 0.4631 | 0.0729 | 0.042 | 1140 | ACSR/TW | 1.245 | 0.4550 | 1586 | 1166.5 | 419.5 | 42,900
TRUCKEE/TW | 1372.5 | 30/7 | 0.0125 | 0.0134 | 0.0158 | 0.4631 | 0.0735 | 0.0409 | 1192 | ACSR/TW | 1.248 | 0.3012 | 1481 | 1293.4 | 187.6 | 33,400
MACKENZIE/TW | 1359.7 | 36/7 | 0.0126 | 0.0134 | 0.0159 | 0.4615 | 0.0729 | 0.042 | 1192 | ACSR/TW | 1.259 | 0.3477 | 1530 | 1280 | 250 | 36,900
THAMES/TW | 1334.6 | 39/19 | 0.0128 | 0.0135 | 0.0161 | 0.4573 | 0.0720 | 0.0436 | 1195 | ACSR/TW | 1.293 | 0.4720 | 1713 | 1261.6 | 451.4 | 46,300
ST._CROIX/TW | 1467.8 | 33/7 | 0.0117 | 0.0126 | 0.0149 | 0.4578 | 0.0726 | 0.0424 | 1241 | ACSR/TW | 1.292 | 0.3123 | 1585 | 1383 | 202 | 35800
MIRAMICHI/TW | 1455.3 | 36/7 | 0.0118 | 0.0126 | 0.0150 | 0.4578 | 0.0723 | 0.0431 | 1241 | ACSR/TW | 1.302 | 0.3600 | 1640 | 1372 | 268 | 39,200
MERRIMACK/TW | 1433.6 | 39/19 | 0.0119 | 0.0126 | 0.0150 | 0.4520 | 0.0713 | 0.045 | 1250 | ACSR/TW | 1.338 | 0.4890 | 1840 | 1356 | 484 | 49,700
PLATTE/TW | 1569.0 | 33/7 | 0.0110 | 0.0118 | 0.0140 | 0.4530 | 0.0718 | 0.0439 | 1291 | ACSR/TW | 1.334 | 0.3222 | 1693 | 1478 | 215 | 38,200
POTOMAC/TW | 1557.4 | 36/7 | 0.0110 | 0.0118 | 0.0140 | 0.4504 | 0.0715 | 0.0445 | 1292 | ACSR/TW | 1.345 | 0.3723 | 1755 | 1468 | 287 | 41,900
RIO_GRANDE/TW | 1533.3 | 39/19 | 0.0112 | 0.0119 | 0.0141 | 0.4472 | 0.0705 | 0.0466 | 1301 | ACSR/TW | 1.382 | 0.5060 | 1968 | 1449 | 519 | 53200
SCHUYLKILL/TW | 1657.4 | 36/7 | 0.0104 | 0.0112 | 0.0132 | 0.4462 | 0.0708 | 0.0459 | 1341 | ACSR/TW | 1.386 | 0.3840 | 1868 | 1563 | 305 | 44,000
PECOS/TW | 1622.0 | 39/19 | 0.0105 | 0.0112 | 0.0132 | 0.4430 | 0.0697 | 0.0481 | 1347 | ACSR/TW | 1.424 | 0.5320 | 2107 | 1533 | 574 | 57,500
PEE_DEE/TW | 1758.6 | 37/7 | 0.0098 | 0.0106 | 0.0125 | 0.4419 | 0.0701 | 0.0473 | 1389 | ACSR/TW | 1.427 | 0.3957 | 1982 | 1658 | 324 | 46700
JAMES/TW | 1730.6 | 39/19 | 0.0099 | 0.0106 | 0.0125 | 0.4377 | 0.0691 | 0.0494 | 1400 | ACSR/TW | 1.465 | 0.5375 | 2221 | 1636 | 585 | 59,400
ATHABASKA/TW | 1949.6 | 42/7 | 0.0088 | 0.0097 | 0.0114 | 0.4340 | 0.0688 | 0.0500 | 1488 | ACSR/TW | 1.504 | 0.4176 | 2199 | 1838 | 361 | 51,900
CUMBERLAND/TW | 1926.9 | 42/19 | 0.0089 | 0.0096 | 0.0113 | 0.4303 | 0.0678 | 0.0523 | 1491 | ACSR/TW | 1.545 | 0.5665 | 2471 | 1821 | 650 | 65,300
POWDER/TW | 2153.8 | 64/19 | 0.0079 | 0.0089 | 0.0104 | 0.4240 | 0.0672 | 0.0538 | 1583 | ACSR/TW | 1.602 | 0.4805 | 2498 | 2030 | 468 | 61,100
SANTEE/TW | 2627.3 | 64/19 | 0.0065 | 0.0076 | 0.0088 | 0.4092 | 0.0649 | 0.0594 | 1768 | ACSR/TW | 1.762 | 0.5310 | 3048 | 2477 | 571 | 74,500
PARTRIDGE/ACSS | 266.8 | 26/7 | 0.0619 | 0.0633 | 0.0760 | 0.565 | 0.088 | 0.0217 | 814 | ACSS | 0.642 | 0.236 | 366.9 | 251.3 | 115.6 | 8,880
LINNET/ACSS | 336.4 | 26/7 | 0.0492 | 0.0502 | 0.0605 | 0.549 | 0.085 | 0.0244 | 943 | ACSS | 0.720 | 0.265 | 462.0 | 316.6 | 145.4 | 11,200
ORIOLE/ACSS | 336.4 | 30/7 | 0.0488 | 0.0498 | 0.0600 | 0.544 | 0.084 | 0.0255 | 955 | ACSS | 0.741 | 0.317 | 526.4 | 317.7 | 208.7 | 14,800
IBIS/ACSS | 397.5 | 26/7 | 0.0416 | 0.0426 | 0.0513 | 0.539 | 0.084 | 0.0265 | 1051 | ACSS | 0.783 | 0.288 | 546.0 | 374.1 | 171.9 | 13,000
LARK/ACSS | 397.5 | 30/7 | 0.0413 | 0.0422 | 0.0507 | 0.533 | 0.082 | 0.0277 | 1069 | ACSS | 0.806 | 0.345 | 621.8 | 375.3 | 246.5 | 17,500
FLICKER/ACSS | 477 | 24/7 | 0.0348 | 0.0357 | 0.0429 | 0.524 | 0.082 | 0.0283 | 1180 | ACSS | 0.846 | 0.282 | 613.9 | 449.4 | 164.5 | 13,000
HAWK/ACSS | 477 | 26/7 | 0.0347 | 0.0356 | 0.0428 | 0.522 | 0.081 | 0.0290 | 1186 | ACSS | 0.858 | 0.316 | 655.3 | 449.0 | 206.3 | 15,600
HEN/ACSS | 477 | 30/7 | 0.0344 | 0.0352 | 0.0424 | 0.517 | 0.080 | 0.3040 | 1200 | ACSS | 0.883 | 0.378 | 746.4 | 450.4 | 296.0 | 21,000
PARAKEET/ACSS | 556.5 | 24/7 | 0.0298 | 0.0305 | 0.0368 | 0.512 | 0.080 | 0.0306 | 1300 | ACSS | 0.914 | 0.304 | 716.1 | 524.3 | 191.8 | 15,200
DOVE/ACSS | 556.5 | 26/7 | 0.0296 | 0.0305 | 0.0366 | 0.510 | 0.080 | 0.0313 | 1316 | ACSS | 0.927 | 0.341 | 765.2 | 524.2 | 241.0 | 18,200
EAGLE/ACSS | 556.5 | 30/7 | 0.0291 | 0.0302 | 0.0362 | 0.505 | 0.079 | 0.0328 | 1336 | ACSS | 0.953 | 0.409 | 870.7 | 525.5 | 345.2 | 24,500
PEACOCK/ACSS | 605 | 24/7 | 0.0274 | 0.0282 | 0.0339 | 0.505 | 0.079 | 0.0319 | 1378 | ACSS | 0.953 | 0.318 | 778.8 | 570.1 | 208.7 | 16,500
ROOK/ACSS | 636 | 24/7 | 0.0260 | 0.0269 | 0.0322 | 0.502 | 0.079 | 0.0327 | 1429 | ACSS | 0.977 | 0.326 | 818.2 | 599.1 | 219.1 | 17,300
GROSBEAK/ACSS | 636 | 26/7 | 0.0259 | 0.0267 | 0.0320 | 0.500 | 0.078 | 0.0335 | 1438 | ACSS | 0.990 | 0.365 | 874.2 | 599.0 | 275.2 | 20,700
EGRET/ACSS | 636 | 30/19 | 0.0258 | 0.0265 | 0.0319 | 0.495 | 0.077 | 0.0351 | 1449 | ACSS | 1.019 | 0.437 | 987.2 | 600.5 | 386.7 | 28,000
FLAMINGO/ACSS | 666.6 | 24/7 | 0.0249 | 0.0256 | 0.0307 | 0.498 | 0.078 | 0.0335 | 1473 | ACSS | 1.000 | 0.333 | 857.9 | 628.2 | 229.7 | 18,200
STARLING/ACSS | 715.5 | 26/7 | 0.0231 | 0.0237 | 0.0285 | 0.490 | 0.077 | 0.0355 | 1550 | ACSS | 1.051 | 0.387 | 983.7 | 674.0 | 309.7 | 23,300
REDWING/ACSS | 715.5 | 30/19 | 0.0229 | 0.0235 | 0.0283 | 0.486 | 0.076 | 0.0372 | 1568 | ACSS | 1.081 | 0.463 | 1109.3 | 675.3 | 434.0 | 30,800
TERN/ACSS | 795 | 45/7 | 0.0210 | 0.0219 | 0.0261 | 0.488 | 0.076 | 0.0352 | 1636 | ACSS | 1.063 | 0.266 | 895 | 748.6 | 146.4 | 14,200
CUCKOO/ACSS | 795 | 24/7 | 0.0209 | 0.0217 | 0.0260 | 0.484 | 0.076 | 0.0361 | 1647 | ACSS | 1.092 | 0.364 | 1023 | 748.8 | 274.2 | 21,700
CONDOR/ACSS | 795 | 54/7 | 0.0209 | 0.0216 | 0.0259 | 0.484 | 0.076 | 0.0368 | 1650 | ACSS | 1.092 | 0.364 | 1022 | 748.4 | 273.6 | 21,700
DRAKE/ACSS | 795 | 26/7 | 0.0210 | 0.0216 | 0.0259 | 0.482 | 0.076 | 0.0375 | 1660 | ACSS | 1.108 | 0.408 | 1093 | 749.1 | 343.9 | 25,900
MALLARD/ACSS | 795 | 30/19 | 0.0207 | 0.0214 | 0.0255 | 0.477 | 0.074 | 0.0392 | 1693 | ACSS | 1.140 | 0.489 | 1233.9 | 750.7 | 483.2 | 34,300
RUDDY/ACSS | 900 | 45/7 | 0.0186 | 0.0194 | 0.0232 | 0.479 | 0.076 | 0.0374 | 1766 | ACSS | 1.131 | 0.283 | 1013 | 847.4 | 165.6 | 15,800
CANARY/ACSS | 900 | 54/7 | 0.0185 | 0.0191 | 0.0230 | 0.474 | 0.074 | 0.0392 | 1780 | ACSS | 1.162 | 0.387 | 1158 | 847.7 | 310.3 | 24,600
RAIL/ACSS | 954 | 45/7 | 0.0172 | 0.0180 | 0.0215 | 0.474 | 0.075 | 0.0385 | 1844 | ACSS | 1.165 | 0.291 | 1074 | 898.5 | 175.5 | 16,700
CARDINAL/ACSS | 954 | 54/7 | 0.0174 | 0.0181 | 0.0217 | 0.470 | 0.076 | 0.0404 | 1856 | ACSS | 1.196 | 0.399 | 1227.1 | 898.3 | 328.8 | 26,000
ORTOLAN/ACSS | 1033.5 | 45/7 | 0.0162 | 0.0170 | 0.0203 | 0.468 | 0.074 | 0.0401 | 1933 | ACSS | 1.212 | 0.303 | 1163 | 972.8 | 190.2 | 18,100
CURLEW/ACSS | 1033.5 | 54/7 | 0.0160 | 0.0167 | 0.0202 | 0.464 | 0.073 | 0.0420 | 1936 | ACSS | 1.246 | 0.415 | 1329 | 972.8 | 356.2 | 28,200
BLUEJAY/ACSS | 1113 | 45/7 | 0.0151 | 0.0158 | 0.0189 | 0.462 | 0.073 | 0.0416 | 2025 | ACSS | 1.259 | 0.315 | 1254 | 1048.7 | 205.3 | 19,500
FINCH/ACSS | 1113 | 54/19 | 0.0150 | 0.0156 | 0.0190 | 0.458 | 0.070 | 0.0436 | 2020 | ACSS | 1.293 | 0.431 | 1430 | 1053.9 | 376.1 | 30,400
BUNTING/ACSS | 1192.5 | 45/7 | 0.0140 | 0.0148 | 0.0177 | 0.456 | 0.072 | 0.0431 | 2116 | ACSS | 1.302 | 0.326 | 1342 | 1123.0 | 219.0 | 21,400
GRACKLE/ACSS | 1192.5 | 54/19 | 0.0140 | 0.0147 | 0.0177 | 0.452 | 0.071 | 0.0451 | 2122 | ACSS | 1.338 | 0.446 | 1531 | 1128.6 | 402.4 | 32,600
BITTERN/ACSS | 1272 | 45/7 | 0.0131 | 0.0140 | 0.0166 | 0.451 | 0.072 | 0.0445 | 2223 | ACSS | 1.345 | 0.336 | 1432 | 1197.7 | 234.3 | 22,300
PHEASANT/ACSS | 1272 | 54/19 | 0.0131 | 0.0138 | 0.0166 | 0.447 | 0.070 | 0.0466 | 2221 | ACSS | 1.382 | 0.461 | 1634 | 1204.3 | 429.7 | 34,100
DIPPER/ACSS | 1351.5 | 45/7 | 0.0123 | 0.0132 | 0.0157 | 0.447 | 0.071 | 0.0459 | 2303 | ACSS | 1.386 | 0.347 | 1521 | 1272.9 | 248.1 | 23,700
MARTIN/ACSS | 1431 | 54/19 | 0.0123 | 0.0130 | 0.0156 | 0.442 | 0.070 | 0.0480 | 2313 | ACSS | 1.424 | 0.475 | 1735 | 1279.2 | 455.8 | 36,200
BOBOLINK/ACSS | 1431 | 45/7 | 0.0117 | 0.0125 | 0.0149 | 0.442 | 0.070 | 0.0472 | 2383 | ACSS | 1.427 | 0.357 | 1611 | 1347.5 | 263.5 | 25,100
PLOVER/ACSS | 1590 | 54/19 | 0.0117 | 0.0123 | 0.0148 | 0.438 | 0.069 | 0.0495 | 2395 | ACSS | 1.465 | 0.489 | 1838 | 1354.6 | 483.4 | 38,400
LAPWING/ACSS | 1590 | 45/7 | 0.0105 | 0.0114 | 0.0135 | 0.434 | 0.069 | 0.0498 | 2559 | ACSS | 1.504 | 0.376 | 1790 | 1498.1 | 291.9 | 27,900
FALCON/ACSS | 1590 | 54/19 | 0.0105 | 0.0113 | 0.0136 | 0.430 | 0.068 | 0.0521 | 2543 | ACSS | 1.545 | 0.515 | 2042 | 1505.0 | 537.0 | 42,600
CHUKAR/ACSS | 1780 | 84/19 | 0.0094 | 0.0103 | 0.0122 | 0.424 | 0.067 | 0.0534 | 2749 | ACSS | 1.602 | 0.437 | 2072 | 1685.5 | 386.5 | 35,400
BLUEBIRD/ACSS | 2156 | 84/19 | 0.0078 | 0.0087 | 0.0103 | 0.409 | 0.065 | 0.0588 | 3089 | ACSS | 1.762 | 0.481 | 2508 | 2040.4 | 467.6 | 42,100
KIWI/ACSS | 2167 | 72/7 | 0.0078 | 0.0089 | 0.0104 | 0.411 | 0.068 | 0.0570 | 3089 | ACSS | 1.735 | 0.347 | 2301 | 2051.4 | 249.6 | 29,000
THRASHER/ACSS | 2312 | 76/19 | 0.0073 | 0.0084 | 0.0098 | 0.405 | 0.065 | 0.0600 | 3227 | ACSS | 1.802 | 0.407 | 2523 | 2187.9 | 335.1 | 35,600
FLICKER/ACSS/TW | 477.0 | 18/7 | 0.0348 | 0.0356 | 0.0427 | 0.5370 | 0.0841 | 0.0257 | 1152 | ACSS/TW | 0.776 | 0.2820 | 612 | 447.7 | 164.3 | 13,000
HAWK/ACSS/TW | 477.0 | 18/7 | 0.0346 | 0.0354 | 0.0426 | 0.5349 | 0.0835 | 0.0264 | 1147 | ACSS/TW | 0.789 | 0.3159 | 655 | 448.2 | 206.8 | 15,600
PARAKEET/ACSS/TW | 556.5 | 18/7 | 0.0297 | 0.0304 | 0.0365 | 0.5248 | 0.0824 | 0.0277 | 1274 | ACSS/TW | 0.835 | 0.3045 | 714 | 522.4 | 191.6 | 15,200
DOVE/ACSS/TW | 556.5 | 20/7 | 0.0296 | 0.0303 | 0.0364 | 0.5232 | 0.0817 | 0.0286 | 1284 | ACSS/TW | 0.852 | 0.3414 | 764 | 522.9 | 241.1 | 18,200
ROOK/ACSS/TW | 636.0 | 18/7 | 0.0260 | 0.0267 | 0.0320 | 0.5164 | 0.0809 | 0.0296 | 1391 | ACSS/TW | 0.890 | 0.3255 | 818 | 597.0 | 221.0 | 17,300
GROSBEAK/ACSS/TW | 636.0 | 20/7 | 0.0259 | 0.0266 | 0.0319 | 0.5127 | 0.0802 | 0.0305 | 1401 | ACSS/TW | 0.908 | 0.3648 | 873 | 597.6 | 275.4 | 20,700
TERN/ACSS/TW | 795.0 | 17/7 | 0.0209 | 0.0216 | 0.0259 | 0.5042 | 0.0797 | 0.0312 | 1583 | ACSS/TW | 0.960 | 0.2658 | 891 | 745.2 | 145.8 | 14,200
PUFFIN/ACSS/TW | 795.0 | 18/7 | 0.0209 | 0.0215 | 0.0258 | 0.5011 | 0.0789 | 0.0323 | 1595 | ACSS/TW | 0.980 | 0.3324 | 974 | 745.9 | 228.1 | 18,900
CONDOR/ACSS/TW | 795.0 | 20/7 | 0.0208 | 0.0214 | 0.0257 | 0.4990 | 0.0784 | 0.0331 | 1604 | ACSS/TW | 0.993 | 0.3639 | 1020 | 746.2 | 273.8 | 21,700
DRAKE/ACSS/TW | 795.0 | 20/7 | 0.0207 | 0.0213 | 0.0255 | 0.4963 | 0.0778 | 0.0339 | 1623 | ACSS/TW | 1.010 | 0.4080 | 1091 | 747.0 | 344.0 | 25,900
PHOENIX/ACSS/TW | 954.0 | 30/7 | 0.0176 | 0.0183 | 0.0219 | 0.4900 | 0.0775 | 0.0343 | 1770 | ACSS/TW | 1.049 | 0.2511 | 1028 | 898.6 | 129.4 | 14,200
RAIL/ACSS/TW | 954.0 | 32/7 | 0.0175 | 0.0182 | 0.0216 | 0.4884 | 0.0771 | 0.0349 | 1803 | ACSS/TW | 1.061 | 0.2913 | 1074 | 897.7 | 176.3 | 16,700
CARDINAL/ACSS/TW | 954.0 | 20/7 | 0.0173 | 0.0179 | 0.0214 | 0.4852 | 0.0763 | 0.0362 | 1814 | ACSS/TW | 1.084 | 0.3987 | 1227 | 895.5 | 331.5 | 26,000
SNOWBIRD/ACSS/TW | 1033.5 | 30/7 | 0.0162 | 0.0169 | 0.0202 | 0.4842 | 0.0767 | 0.0356 | 1870 | ACSS/TW | 1.089 | 0.2613 | 1114 | 972.5 | 141.5 | 15,400
ORTOLAN/ACSS/TW | 1033.5 | 32/7 | 0.0162 | 0.0169 | 0.0202 | 0.4826 | 0.0762 | 0.0363 | 1877 | ACSS/TW | 1.102 | 0.3030 | 1163 | 973.4 | 189.6 | 18,100
CURLEW/ACSS/TW | 1033.5 | 21/7 | 0.0160 | 0.0167 | 0.0199 | 0.4784 | 0.0754 | 0.0377 | 1911 | ACSS/TW | 1.129 | 0.4149 | 1326 | 970.1 | 355.9 | 28,200
AVOCET/ACSS/TW | 1113.0 | 30/7 | 0.0150 | 0.0157 | 0.0188 | 0.4784 | 0.0758 | 0.0369 | 1959 | ACSS/TW | 1.129 | 0.2712 | 1199 | 1047.3 | 151.7 | 16,300
BLUEJAY/ACSS/TW | 1113.0 | 33/7 | 0.0150 | 0.0157 | 0.0187 | 0.4768 | 0.0754 | 0.0376 | 1980 | ACSS/TW | 1.143 | 0.3147 | 1253 | 1048.3 | 204.7 | 19,500
FINCH/ACSS/TW | 1113.0 | 38/19 | 0.0149 | 0.0156 | 0.0185 | 0.4704 | 0.0740 | 0.0399 | 2020 | ACSS/TW | 1.185 | 0.4310 | 1427 | 1050.9 | 376.1 | 30,400
OXBIRD/ACSS/TW | 1192.5 | 30/7 | 0.0140 | 0.0148 | 0.0176 | 0.4730 | 0.0750 | 0.0382 | 2057 | ACSS/TW | 1.167 | 0.2808 | 1285 | 1122.1 | 162.9 | 17,500
BUNTING/ACSS/TW | 1192.5 | 33/7 | 0.0140 | 0.0147 | 0.0175 | 0.4715 | 0.0746 | 0.0390 | 2069 | ACSS/TW | 1.181 | 0.3255 | 1342 | 1123.2 | 218.8 | 20,900
GRACKLE/ACSS/TW | 1192.5 | 38/19 | 0.0140 | 0.0146 | 0.0175 | 0.4662 | 0.0733 | 0.0412 | 2083 | ACSS/TW | 1.225 | 0.4460 | 1529 | 1125.9 | 403.1 | 32,600
SCISSORTAIL/ACSS/TW | 1272.0 | 30/7 | 0.0132 | 0.0140 | 0.0166 | 0.4689 | 0.0743 | 0.0394 | 2143 | ACSS/TW | 1.203 | 0.2901 | 1371 | 1196.9 | 174.1 | 18,700
BITTERN/ACSS/TW | 1272.0 | 35/7 | 0.0131 | 0.0138 | 0.0164 | 0.4667 | 0.0738 | 0.0403 | 2162 | ACSS/TW | 1.220 | 0.3363 | 1432 | 1198.1 | 233.9 | 22,300
PHEASANT/ACSS/TW | 1272.0 | 39/19 | 0.0131 | 0.0138 | 0.0164 | 0.4615 | 0.0725 | 0.0426 | 2188 | ACSS/TW | 1.264 | 0.4605 | 1630 | 1201.0 | 429.0 | 34,100
DIPPER/ACSS/TW | 1351.5 | 35/7 | 0.0124 | 0.0131 | 0.0156 | 0.4615 | 0.0731 | 0.0415 | 2235 | ACSS/TW | 1.256 | 0.3465 | 1521 | 1273.0 | 248.0 | 23,700
MARTIN/ACSS/TW | 1351.5 | 39/19 | 0.0123 | 0.0130 | 0.0154 | 0.4567 | 0.0714 | 0.0438 | 2284 | ACSS/TW | 1.300 | 0.4745 | 1732 | 1276.1 | 455.9 | 36,200
BOBOLINK/ACSS/TW | 1431.0 | 36/7 | 0.0117 | 0.0125 | 0.0148 | 0.4578 | 0.0725 | 0.0427 | 2325 | ACSS/TW | 1.291 | 0.3567 | 1611 | 1347.8 | 263.2 | 25,100
PLOVER/ACSS/TW | 1431.0 | 39/19 | 0.0116 | 0.0123 | 0.0146 | 0.4541 | 0.0712 | 0.0451 | 2363 | ACSS/TW | 1.337 | 0.4885 | 1834 | 1351.1 | 483.0 | 38,400
LAPWING/ACSS/TW | 1590.0 | 36/7 | 0.0105 | 0.0113 | 0.0133 | 0.4493 | 0.0714 | 0.0449 | 2505 | ACSS/TW | 1.358 | 0.3759 | 1790 | 1497.6 | 292.4 | 27,900
FALCON/ACSS/TW | 1590.0 | 42/19 | 0.0105 | 0.0112 | 0.0133 | 0.4441 | 0.0700 | 0.0476 | 2518 | ACSS/TW | 1.408 | 0.5150 | 2038 | 1501.3 | 536.7 | 42,600
CHUKAR/ACSS/TW | 1780.0 | 37/19 | 0.0095 | 0.0103 | 0.0122 | 0.4393 | 0.0697 | 0.0482 | 2657 | ACSS/TW | 1.445 | 0.4370 | 2061 | 1674.1 | 386.9 | 35,300
BLUEBIRD/ACSS/TW | 2156.0 | 64/19 | 0.0078 | 0.0087 | 0.0102 | 0.4229 | 0.0672 | 0.0538 | 3034 | ACSS/TW | 1.608 | 0.4805 | 2512 | 2044.6 | 467.4 | 42,100
MOHAWK/ACSS/TW | 571.7 | 18/7 | 0.0287 | 0.0295 | 0.0353 | 0.5232 | 0.0821 | 0.0281 | 1306 | ACSS/TW | 0.846 | 0.3090 | 734 | 536.6 | 197.4 | 15,600
CALUMET/ACSS/TW | 565.3 | 20/7 | 0.0294 | 0.0300 | 0.0359 | 0.5217 | 0.0815 | 0.0304 | 1300 | ACSS/TW | 0.858 | 0.3438 | 776 | 531.2 | 244.8 | 18,400
MYSTIC/ACSS/TW | 666.6 | 20/7 | 0.0248 | 0.0256 | 0.0306 | 0.5122 | 0.0803 | 0.0310 | 1435 | ACSS/TW | 0.913 | 0.3330 | 856 | 625.7 | 230.3 | 18,200
OSWEGO/ACSS/TW | 664.8 | 20/7 | 0.0250 | 0.0255 | 0.0306 | 0.5090 | 0.0798 | 0.0325 | 1441 | ACSS/TW | 0.927 | 0.3732 | 913 | 624.6 | 288.4 | 21,700
WABASH/ACSS/TW | 762.8 | 20/7 | 0.0216 | 0.0223 | 0.0267 | 0.5011 | 0.0788 | 0.0330 | 1576 | ACSS/TW | 0.977 | 0.3585 | 987 | 721.1 | 265.9 | 21,000
KETTLE/ACSS/TW | 957.2 | 32/7 | 0.0174 | 0.0182 | 0.0219 | 0.4994 | 0.0784 | 0.0350 | 1772 | ACSS/TW | 0.990 | 0.3993 | 1047 | 716.7 | 330.3 | 24,900
MAUMEE/ACSS/TW | 768.2 | 20/7 | 0.0215 | 0.0221 | 0.0265 | 0.4884 | 0.0770 | 0.0325 | 1570 | ACSS/TW | 1.060 | 0.2919 | 1078 | 901.6 | 176.4 | 16,800
FRASER/ACSS/TW | 946.7 | 35/7 | 0.0177 | 0.0184 | 0.0219 | 0.4852 | 0.0765 | 0.0358 | 1797 | ACSS/TW | 1.077 | 0.3462 | 1140 | 892.6 | 247.4 | 21,100
COLUMBIA/ACSS/TW | 966.2 | 21/7 | 0.0163 | 0.0170 | 0.0219 | 0.4842 | 0.0761 | 0.0364 | 1820 | ACSS/TW | 1.092 | 0.4014 | 1240 | 906.9 | 333.1 | 26,400
SUWANNEE/ACSS/TW | 959.6 | 22/7 | 0.0178 | 0.0187 | 0.0213 | 0.4821 | 0.0756 | 0.0373 | 1831 | ACSS/TW | 1.108 | 0.4479 | 1317 | 901.6 | 415.4 | 30,700
CHEYENNE/ACSS/TW | 1168.1 | 30/7 | 0.0143 | 0.0152 | 0.0180 | 0.4757 | 0.0753 | 0.0378 | 2036 | ACSS/TW | 1.155 | 0.2778 | 1259 | 1099.2 | 159.8 | 17,200
GENESSEE/ACSS/TW | 1158.0 | 33/7 | 0.0144 | 0.0152 | 0.0181 | 0.4736 | 0.0749 | 0.0384 | 2028 | ACSS/TW | 1.165 | 0.3234 | 1307 | 1090.7 | 216.3 | 20,500
HUDSON/ACSS/TW | 1158.4 | 25/7 | 0.0142 | 0.0150 | 0.0179 | 0.4694 | 0.0740 | 0.0400 | 2052 | ACSS/TW | 1.196 | 0.4401 | 1488 | 1087.4 | 400.6 | 31,100
CATAWBA/ACSS/TW | 1272.0 | 30/7 | 0.0131 | 0.0140 | 0.0164 | 0.4694 | 0.0743 | 0.0394 | 2175 | ACSS/TW | 1.203 | 0.2901 | 1371 | 1196.9 | 174.1 | 18,700
NELSON/ACSS/TW | 1257.1 | 35/7 | 0.0132 | 0.0141 | 0.0167 | 0.4678 | 0.0740 | 0.0400 | 2143 | ACSS/TW | 1.213 | 0.3345 | 1416 | 1184.1 | 231.9 | 22,100
YUKON/ACSS/TW | 1233.6 | 38/19 | 0.0134 | 0.0142 | 0.0168 | 0.4631 | 0.0729 | 0.0420 | 2161 | ACSS/TW | 1.245 | 0.4550 | 1584 | 1164.8 | 419.2 | 33,200
TRUCKEE/ACSS/TW | 1372.5 | 30/7 | 0.0121 | 0.0131 | 0.0155 | 0.4631 | 0.0735 | 0.0409 | 2249 | ACSS/TW | 1.248 | 0.3012 | 1479 | 1291.5 | 187.5 | 20,200
MACKENZIE/ACSS/TW | 1359.7 | 36/7 | 0.0122 | 0.0131 | 0.0156 | 0.4615 | 0.0729 | 0.0420 | 2237 | ACSS/TW | 1.259 | 0.3477 | 1531 | 1280.7 | 250.3 | 23,900
THAMES/ACSS/TW | 1334.6 | 39/19 | 0.0124 | 0.0132 | 0.0156 | 0.4573 | 0.0720 | 0.0436 | 2267 | ACSS/TW | 1.293 | 0.4720 | 1711 | 1260.1 | 450.9 | 35,800
ST._CROIX/ACSS/TW | 1467.8 | 33/7 | 0.0114 | 0.0123 | 0.0146 | 0.4578 | 0.0726 | 0.0424 | 2336 | ACSS/TW | 1.292 | 0.3123 | 1583 | 1381.2 | 201.8 | 21600
MIRAMICHI/ACSS/TW | 1455.3 | 36/7 | 0.0114 | 0.0117 | 0.0146 | 0.4578 | 0.0723 | 0.0431 | 2260 | ACSS/TW | 1.302 | 0.3600 | 1639 | 1370.7 | 268.3 | 25,600
MERRIMACK/ACSS/TW | 1433.6 | 39/19 | 0.0115 | 0.0123 | 0.0146 | 0.4520 | 0.0713 | 0.0450 | 2365 | ACSS/TW | 1.338 | 0.4890 | 1838 | 1353.6 | 484.4 | 38,400
PLATTE/ACSS/TW | 1569.0 | 33/7 | 0.0106 | 0.0116 | 0.0137 | 0.4530 | 0.0718 | 0.0439 | 2445 | ACSS/TW | 1.334 | 0.3222 | 1691 | 1476.4 | 214.6 | 23,100
POTOMAC/ACSS/TW | 1557.4 | 36/7 | 0.0106 | 0.0116 | 0.0136 | 0.4504 | 0.0715 | 0.0445 | 2480 | ACSS/TW | 1.345 | 0.3723 | 1754 | 1466.9 | 287.1 | 27,300
RIO_GRANDE/ACSS/TW | 1533.3 | 39/19 | 0.0108 | 0.0116 | 0.0137 | 0.4472 | 0.0705 | 0.0466 | 2475 | ACSS/TW | 1.382 | 0.5060 | 1966 | 1447.7 | 518.3 | 41200
SCHUYLKILL/ACSS/TW | 1657.4 | 36/7 | 0.0100 | 0.0110 | 0.0130 | 0.4462 | 0.0708 | 0.0459 | 2545 | ACSS/TW | 1.386 | 0.3840 | 1866 | 1561.1 | 304.9 | 29,100
PECOS/ACSS/TW | 1622.0 | 39/19 | 0.0102 | 0.0110 | 0.0130 | 0.4430 | 0.0697 | 0.0481 | 2563 | ACSS/TW | 1.424 | 0.5320 | 2105 | 1531.5 | 573.5 | 45,000
PEE_DEE/ACSS/TW | 1758.6 | 37/7 | 0.0095 | 0.0103 | 0.0121 | 0.4419 | 0.0701 | 0.0473 | 2675 | ACSS/TW | 1.427 | 0.3957 | 1980 | 1656.4 | 323.6 | 30900
JAMES/ACSS/TW | 1730.6 | 39/19 | 0.0095 | 0.0097 | 0.0123 | 0.4377 | 0.0691 | 0.0494 | 2537 | ACSS/TW | 1.465 | 0.5375 | 2219 | 1634.0 | 585.0 | 46,400
ATHABASKA/ACSS/TW | 1949.6 | 42/7 | 0.0095 | 0.0096 | 0.0112 | 0.4340 | 0.0688 | 0.0500 | 2840 | ACSS/TW | 1.504 | 0.4176 | 2197 | 1836.3 | 360.7 | 34,300
CUMBERLAND/ACSS/TW | 1926.9 | 42/19 | 0.0086 | 0.0095 | 0.0111 | 0.4303 | 0.0678 | 0.0523 | 2881 | ACSS/TW | 1.545 | 0.5665 | 2469 | 1819.4 | 649.6 | 51,600
POWDER/ACSS/TW | 2153.8 | 64/19 | 0.0075 | 0.0087 | 0.0101 | 0.4240 | 0.0672 | 0.0538 | 3067 | ACSS/TW | 1.602 | 0.4805 | 2510 | 2042.5 | 467.5 | 42,100
SANTEE/ACSS/TW | 2627.3 | 64/19 | 0.0064 | 0.0085 | 0.0097 | 0.4092 | 0.0649 | 0.0594 | 3379 | ACSS/TW | 1.762 | 0.5310 | 3063 | 2491.5 | 571.5 | 51,300
PEACHBELL | 6 | 7 | 0.6593 | 0.6725 | 0.8059 | 0.7660 | 0.1193 | 0.00555 | 103 | AAC | 0.184 |  | 24.6 |  |  | 563
ROSE | 4 | 7 | 0.4144 | 0.4227 | 0.5064 | 0.7296 | 0.1140 | 0.00700 | 138 | AAC | 0.232 |  | 39.1 |  |  | 881
IRIS | 2 | 7 | 0.2602 | 0.2655 | 0.3182 | 0.6929 | 0.1087 | 0.00883 | 185 | AAC | 0.292 |  | 62.2 |  |  | 1350
PANSY | 1 | 7 | 0.2066 | 0.2110 | 0.2527 | 0.6716 | 0.1061 | 0.00991 | 214 | AAC | 0.328 |  | 78.4 |  |  | 1640
POPPY | 1/0 | 7 | 0.1638 | 0.1671 | 0.2002 | 0.6550 | 0.1034 | 0.0111 | 247 | AAC | 0.368 |  | 98.9 |  |  | 1990
ASTER | 2/0 | 7 | 0.1299 | 0.1326 | 0.1587 | 0.6346 | 0.1008 | 0.0125 | 286 | AAC | 0.414 |  | 124.8 |  |  | 2510
PHLOX | 3/0 | 7 | 0.1031 | 0.1053 | 0.1259 | 0.6188 | 0.0981 | 0.0140 | 331 | AAC | 0.464 |  | 157.2 |  |  | 3040
OXLIP | 4/0 | 7 | 0.0817 | 0.0835 | 0.1000 | 0.6029 | 0.0955 | 0.0158 | 383 | AAC | 0.522 |  | 198.4 |  |  | 3830
SNEEZEWORT | 250.0 | 7 | 0.0691 | 0.0706 | 0.0847 | 0.586 | 0.0934 | 0.0171 | 425 | AAC | 0.567 |  | 234.4 |  |  | 4520
VALERIAN | 250.0 | 19 | 0.0691 | 0.0706 | 0.0847 | 0.586 | 0.0922 | 0.0181 | 425 | AAC | 0.574 |  | 234.3 |  |  | 4660
DAISY | 266.8 | 7 | 0.0648 | 0.0663 | 0.0794 | 0.581 | 0.0926 | 0.0177 | 443 | AAC | 0.586 |  | 250.2 |  |  | 4830
LAUREL | 266.8 | 19 | 0.0648 | 0.0663 | 0.0794 | 0.581 | 0.0915 | 0.0187 | 444 | AAC | 0.593 |  | 250.1 |  |  | 4970
PEONY | 300.0 | 19 | 0.0575 | 0.0589 | 0.0705 | 0.570 | 0.0902 | 0.0198 | 478 | AAC | 0.629 |  | 281.4 |  |  | 5480
TULIP | 336.4 | 19 | 0.0513 | 0.0527 | 0.0629 | 0.560 | 0.0888 | 0.0210 | 512 | AAC | 0.666 |  | 315.5 |  |  | 6150
DAFFODIL | 350.0 | 19 | 0.0494 | 0.0506 | 0.0606 | 0.560 | 0.0883 | 0.0214 | 526 | AAC | 0.679 |  | 327.9 |  |  | 6390
CANNA | 397.5 | 19 | 0.0435 | 0.0445 | 0.0534 | 0.549 | 0.0869 | 0.0228 | 570 | AAC | 0.724 |  | 372.9 |  |  | 7110
GOLDENTUFT | 450.0 | 19 | 0.0384 | 0.0394 | 0.0472 | 0.539 | 0.0854 | 0.0243 | 616 | AAC | 0.769 |  | 421.8 |  |  | 7890
COSMOS | 477.0 | 19 | 0.0363 | 0.0373 | 0.0445 | 0.533 | 0.0848 | 0.0250 | 639 | AAC | 0.792 |  | 446.8 |  |  | 8360
SYRINGA | 477.0 | 37 | 0.0363 | 0.0373 | 0.0445 | 0.533 | 0.0845 | 0.0254 | 639 | AAC | 0.795 |  | 446.8 |  |  | 8690
ZINNIA | 500.0 | 19 | 0.0346 | 0.0356 | 0.0426 | 0.531 | 0.0843 | 0.0256 | 658 | AAC | 0.811 |  | 468.5 |  |  | 8760
DAHLIA | 556.5 | 19 | 0.0311 | 0.0320 | 0.0383 | 0.522 | 0.0830 | 0.0270 | 703 | AAC | 0.856 |  | 521.4 |  |  | 9750
MISTLETOE | 556.5 | 37 | 0.0311 | 0.0320 | 0.0383 | 0.522 | 0.0826 | 0.0275 | 704 | AAC | 0.858 |  | 521.3 |  |  | 9940
MEADOWSWEET | 600.0 | 37 | 0.0288 | 0.0297 | 0.0356 | 0.516 | 0.0818 | 0.0285 | 738 | AAC | 0.891 |  | 562 |  |  | 10700
ORCHID | 636.0 | 37 | 0.0272 | 0.0282 | 0.0335 | 0.511 | 0.0811 | 0.0294 | 765 | AAC | 0.918 |  | 596 |  |  | 11400
HEUCHERA | 650.0 | 37 | 0.0266 | 0.0275 | 0.0324 | 0.510 | 0.0808 | 0.0297 | 775 | AAC | 0.928 |  | 609.8 |  |  | 11600
VERBENA | 700.0 | 37 | 0.0247 | 0.0256 | 0.0305 | 0.504 | 0.0799 | 0.0308 | 812 | AAC | 0.963 |  | 655.7 |  |  | 12500
VIOLET | 715.5 | 37 | 0.0242 | 0.0252 | 0.0299 | 0.502 | 0.0797 | 0.0312 | 823 | AAC | 0.974 |  | 671 |  |  | 12800
NASTURTIUM | 715.5 | 61 | 0.0242 | 0.0252 | 0.0299 | 0.502 | 0.0795 | 0.0314 | 823 | AAC | 0.975 |  | 671 |  |  | 13100
PETUNIA | 750.0 | 37 | 0.0230 | 0.0251 | 0.0286 | 0.498 | 0.0792 | 0.0319 | 847 | AAC | 0.997 |  | 703.2 |  |  | 13100
ARBUTUS | 795.0 | 37 | 0.0217 | 0.0227 | 0.0269 | 0.494 | 0.0780 | 0.0328 | 878 | AAC | 1.026 |  | 745.3 |  |  | 13900
LILAC | 795.0 | 61 | 0.0217 | 0.0227 | 0.0269 | 0.494 | 0.0784 | 0.0331 | 879 | AAC | 1.028 |  | 745.7 |  |  | 14300
COCKSCOMB | 900.0 | 37 | 0.0192 | 0.0201 | 0.0239 | 0.484 | 0.0771 | 0.0349 | 948 | AAC | 1.092 |  | 844 |  |  | 16400
MAGNOLIA | 954.0 | 37 | 0.0181 | 0.0191 | 0.0227 | 0.479 | 0.0763 | 0.0360 | 982 | AAC | 1.124 |  | 894.5 |  |  | 16400
GOLDENROD | 954.0 | 61 | 0.0181 | 0.0191 | 0.0227 | 0.479 | 0.0763 | 0.0362 | 983 | AAC | 1.126 |  | 894.8 |  |  | 16900
HAWKWEED | 1000.0 | 37 | 0.0173 | 0.0182 | 0.0216 | 0.476 | 0.0759 | 0.0368 | 1010 | AAC | 1.151 |  | 937.3 |  |  | 17200
BLUEBELL | 1033.5 | 37 | 0.0167 | 0.0177 | 0.0210 | 0.473 | 0.0756 | 0.0374 | 103 | AAC | 1.17 |  | 968.4 |  |  | 17700
LARKSPUR | 1033.5 | 61 | 0.0167 | 0.0177 | 0.0210 | 0.473 | 0.0754 | 0.0377 | 1032 | AAC | 1.172 |  | 969.2 |  |  | 18300
MARIGOLD | 1113.0 | 61 | 0.0155 | 0.0165 | 0.0195 | 0.467 | 0.0744 | 0.0391 | 1079 | AAC | 1.216 |  | 1044 |  |  | 19700
HAWTHORN | 1192.5 | 61 | 0.0145 | 0.0155 | 0.0183 | 0.462 | 0.0737 | 0.0405 | 1124 | AAC | 1.258 |  | 1117 |  |  | 21100
NARCISSUS | 1272.0 | 61 | 0.0136 | 0.0146 | 0.0173 | 0.457 | 0.0729 | 0.0418 | 1169 | AAC | 1.3 |  | 1192 |  |  | 22000
COLUMBINE | 1351.5 | 61 | 0.0128 | 0.0138 | 0.0163 | 0.452 | 0.0722 | 0.0431 | 1212 | AAC | 1.34 |  | 1266 |  |  | 23400
CARNATION | 1431.0 | 61 | 0.0121 | 0.0132 | 0.0155 | 0.447 | 0.0715 | 0.0444 | 1253 | AAC | 1.379 |  | 1342 |  |  | 24300
COREOPSIS | 1590.0 | 61 | 0.0109 | 0.0120 | 0.0141 | 0.439 | 0.0705 | 0.0468 | 1333 | AAC | 1.454 |  | 1489 |  |  | 27000
JESSAMINE | 1750.0 | 61 | 0.0099 | 0.0111 | 0.0129 | 0.432 | 0.0693 | 0.0490 | 1408 | AAC | 1.525 |  | 1641 |  |  | 29700
COWSLIP | 2000.0 | 91 | 0.0087 | 0.0099 | 0.0115 | 0.421 | 0.0677 | 0.0525 | 1518 | AAC | 1.63 |  | 1873 |  |  | 34200
LUPINE | 2500.0 | 91 | 0.0070 | 0.0084 | 0.0097 | 0.404 | 0.0652 | 0.0588 | 1706 | AAC | 1.823 |  | 2365 |  |  | 41900
TRILLIUM | 3000.0 | 127 | 0.0058 | 0.0074 | 0.0084 | 0.389 | 0.0629 | 0.0646 | 1874 | AAC | 1.998 |  | 2840 |  |  | 50300
BLUEBONNET | 3500.0 | 127 | 0.0050 | 0.0068 | 0.0076 | 0.378 | 0.0612 | 0.0697 | 2024 | AAC | 2.158 |  | 3345 |  |  | 58700
AKRON | 30.58 | 7 | 0.6589 | 0.670 | 0.784 | 0.751 | 0.118 | 0.00599 | 107 | AAAC | 0.198 |  | 28.5 |  |  | 1,110
ALTON | 48.69 | 7 | 0.4138 | 0.420 | 0.492 | 0.715 | 0.112 | 0.00756 | 143 | AAAC | 0.250 |  | 45.4 |  |  | 1,760
AMES | 77.47 | 7 | 0.2600 | 0.265 | 0.311 | 0.678 | 0.107 | 0.00954 | 191 | AAAC | 0.316 |  | 72.2 |  |  | 2,800
AZUSA | 123.3 | 7 | 0.1635 | 0.166 | 0.195 | 0.642 | 0.102 | 0.0120 | 156 | AAAC | 0.398 |  | 114.9 |  |  | 4,270
ANAHEIM | 155.4 | 7 | 0.1297 | 0.132 | 0.155 | 0.624 | 0.0989 | 0.0135 | 196 | AAAC | 0.447 |  | 144.9 |  |  | 5,390
AMHERST | 195.7 | 7 | 0.1030 | 0.105 | 0.123 | 0.606 | 0.0963 | 0.0152 | 342 | AAAC | 0.502 |  | 182.5 |  |  | 6,790
ALLIANCE | 246.9 | 7 | 0.0816 | 0.0831 | 0.0973 | 0.588 | 0.0936 | 0.0170 | 395 | AAAC | 0.563 |  | 230.2 |  |  | 8,560
BUTTE | 312.8 | 19 | 0.0644 | 0.0657 | 0.0769 | 0.567 | 0.0896 | 0.0202 | 460 | AAAC | 0.642 |  | 291.6 |  |  | 10,500
CANTON | 394.5 | 19 | 0.0511 | 0.0523 | 0.0610 | 0.549 | 0.0870 | 0.0227 | 532 | AAAC | 0.721 |  | 367.9 |  |  | 13,300
CAIRO | 465.4 | 19 | 0.0433 | 0.0443 | 0.0517 | 0.536 | 0.0851 | 0.0247 | 590 | AAAC | 0.783 |  | 433.9 |  |  | 15,600
DARIEN | 559.5 | 19 | 0.0360 | 0.0369 | 0.0431 | 0.522 | 0.0829 | 0.0271 | 663 | AAAC | 0.858 |  | 521.7 |  |  | 18,800
ELGIN | 652.4 | 19 | 0.0309 | 0.0318 | 0.0371 | 0.510 | 0.0812 | 0.0292 | 729 | AAAC | 0.927 |  | 608.3 |  |  | 21,900
FLINT | 740.8 | 37 | 0.0272 | 0.0280 | 0.0328 | 0.499 | 0.0793 | 0.0317 | 790 | AAAC | 0.991 |  | 690.8 |  |  | 24,400
GREELEY | 927.2 | 37 | 0.0217 | 0.0225 | 0.0263 | 0.482 | 0.0768 | 0.0354 | 908 | AAAC | 1.108 |  | 864.6 |  |  | 30,500
PARTRIDGE/SD | 266.8 | 16 | 0.0637 | 0.3433 | 0.4111 | 0.1073 | 0.4628 | 0.0220 | 449 | ACSR/SD | 0.645 | 0.236 | 66.32 | 13,000 | 367 | 11,350
LINNET/SD | 336.4 | 16 | 0.0505 | 0.2726 | 0.3263 | 0.1042 | 0.4503 | 0.0245 | 519 | ACSR/SD | 0.716 | 0.265 | 68.38 | 13,000 | 462.4 | 14,300
HAWK/SD | 477 | 16 | 0.0356 | 0.1926 | 0.2305 | 0.0988 | 0.4293 | 0.0291 | 641 | ACSR/SD | 0.860 | 0.316 | 84.36 | 11,000 | 655.8 | 19,500
BLACKBIRD | 556.5 | 5 | 0.0309 | 0.1676 | 0.2003 | 0.0993 | 0.4365 | 0.0274 | 645 | ACSR/SD | 0.843 | 0.169 | 68.38 | 10,000 | 599 | 13,600
PARAKEET/SD | 556.5 | 13 | 0.0307 | 0.1659 | 0.1984 | 0.0974 | 0.4246 | 0.0302 | 706 | ACSR/SD | 0.901 | 0.305 | 84.36 | 10,000 | 716 | 20,000
DOVE/SD | 556.5 | 16 | 0.0305 | 0.1651 | 0.1975 | 0.0968 | 0.4212 | 0.0311 | 750 | ACSR/SD | 0.919 | 0.341 | 84.36 | 10,000 | 765 | 22,600
GROSBEAK/SD | 636 | 16 | 0.0267 | 0.1447 | 0.1730 | 0.0950 | 0.4142 | 0.0329 | 766 | ACSR/SD | 0.975 | 0.365 | 84.36 | 9,000 | 874 | 25,400
MACAW/SD | 795 | 5 | 0.0217 | 0.1181 | 0.1409 | 0.0943 | 0.4153 | 0.0326 | 772 | ACSR/SD | 0.999 | 0.229 | 90.45 | 14,000 | 856 | 19,800
TERN/SD | 795 | 7 | 0.0216 | 0.1176 | 0.1404 | 0.0939 | 0.4128 | 0.0333 | 869 | ACSR/SD | 1.013 | 0.266 | 90.45 | 13,000 | 893 | 21,900
PUFFIN/SD | 795 | 10 | 0.0215 | 0.1172 | 0.1399 | 0.0933 | 0.4092 | 0.0343 | 876 | ACSR/SD | 1.034 | 0.317 | 90.45 | 13,000 | 956 | 25,100
CONDOR/SD | 795 | 13 | 0.0215 | 0.1166 | 0.1393 | 0.0927 | 0.4058 | 0.0353 | 880 | ACSR/SD | 1.055 | 0.364 | 90.45 | 12,000 | 1023 | 28,200
DRAKE/SD | 795 | 16 | 0.0214 | 0.1160 | 0.1386 | 0.0921 | 0.4022 | 0.0364 | 887 | ACSR/SD | 1.077 | 0.408 | 90.45 | 11,000 | 1093 | 31,800
PHOENIX/SD | 954 | 5 | 0.0180 | 0.0988 | 0.1177 | 0.0918 | 0.4046 | 0.0357 | 967 | ACSR/SD | 1.088 | 0.251 | 90.45 | 11,000 | 1027 | 23,700
RAIL/SD | 954 | 7 | 0.0180 | 0.0985 | 0.1174 | 0.0914 | 0.4021 | 0.0364 | 973 | ACSR/SD | 1.103 | 0.291 | 90.45 | 11,000 | 1073 | 26,100
CARDINAL/SD | 954 | 13 | 0.0179 | 0.0976 | 0.1164 | 0.0902 | 0.3956 | 0.0384 | 985 | ACSR/SD | 1.147 | 0.399 | 90.45 | 10,000 | 1227 | 33,500
SNOWBIRD/SD | 1033.5 | 5 | 0.0167 | 0.0922 | 0.1097 | 0.0892 | 0.3941 | 0.0389 | 1017 | ACSR/SD | 1.185 | 0.261 | 90.45 | 10,000 | 1115 | 25,900
ORTOLAN/SD | 1033.5 | 7 | 0.0166 | 0.0917 | 0.1086 | 0.0903 | 0.3975 | 0.0378 | 1021 | ACSR/SD | 1.145 | 0.303 | 90.45 | 10,000 | 1161 | 28,100
CURLEW/SD | 1033.5 | 13 | 0.0165 | 0.0902 | 0.1076 | 0.0891 | 0.3908 | 0.0400 | 1036 | ACSR/SD | 1.191 | 0.415 | 90.45 | 9,000 | 1329 | 36,300
AVOCET/SD | 1113 | 5 | 0.0155 | 0.0860 | 0.1021 | 0.0882 | 0.3900 | 0.0402 | 1063 | ACSR/SD | 1.226 | 0.271 | 90.45 | 9,000 | 1200 | 27,500
BLUEJAY/SD | 1113 | 7 | 0.0155 | 0.0855 | 0.1016 | 0.0878 | 0.3875 | 0.0410 | 1069 | ACSR/SD | 1.242 | 0.315 | 90.45 | 9,000 | 1254 | 30,300
FINCH/SD | 1113 | 13 | 0.0153 | 0.0840 | 0.1001 | 0.0881 | 0.3865 | 0.0414 | 1084 | ACSR/SD | 1.233 | 0.431 | 90.45 | 9,000 | 1424 | 39,100
OXBIRD/SD | 1192.5 | 5 | 0.0145 | 0.0806 | 0.0956 | 0.0873 | 0.3863 | 0.0415 | 1111 | ACSR/SD | 1.266 | 0.281 | 90.45 | 9,000 | 1286 | 29,500
BUNTING/SD | 1192.5 | 7 | 0.0144 | 0.0802 | 0.0952 | 0.0869 | 0.3836 | 0.0423 | 1114 | ACSR/SD | 1.284 | 0.326 | 90.45 | 8,000 | 1343 | 32,400
GRACKLE/SD | 1192.5 | 13 | 0.0143 | 0.0786 | 0.0936 | 0.0871 | 0.3824 | 0.0428 | 1130 | ACSR/SD | 1.274 | 0.446 | 90.45 | 8,000 | 1526 | 41,900
SCISSORTAIL/SD | 1272 | 5 | 0.0136 | 0.0759 | 0.0899 | 0.0864 | 0.3827 | 0.0427 | 1153 | ACSR/SD | 1.305 | 0.290 | 96.60 | 12,000 | 1372 | 31,400
BITTERN/SD | 1272 | 7 | 0.0135 | 0.0755 | 0.0896 | 0.0860 | 0.3800 | 0.0436 | 1159 | ACSR/SD | 1.323 | 0.336 | 96.60 | 12,000 | 1433 | 34,600
PHEASANT/SD | 1272 | 13 | 0.0134 | 0.0743 | 0.0883 | 0.0848 | 0.3725 | 0.0464 | 1176 | ACSR/SD | 1.378 | 0.461 | 96.60 | 12,000 | 1631 | 44,100
DIPPER/SD | 1351.5 | 7 | 0.0128 | 0.0715 | 0.0846 | 0.0851 | 0.3767 | 0.0449 | 1202 | ACSR/SD | 1.361 | 0.347 | 96.60 | 12,000 | 1522 | 36,700
MARTIN/SD | 1351.5 | 13 | 0.0126 | 0.0702 | 0.0833 | 0.0839 | 0.3691 | 0.0477 | 1219 | ACSR/SD | 1.417 | 0.475 | 96.60 | 11,000 | 1733 | 46,800
BOBOLINK/SD | 1431 | 7 | 0.0120 | 0.0678 | 0.0801 | 0.0843 | 0.3734 | 0.0461 | 1243 | ACSR/SD | 1.398 | 0.357 | 96.60 | 11,000 | 1612 | 38,900
PLOVER/SD | 1431 | 13 | 0.0120 | 0.0669 | 0.0792 | 0.0833 | 0.3666 | 0.0488 | 1262 | ACSR/SD | 1.448 | 0.489 | 96.60 | 11,000 | 1835 | 49,600
LAPWING/SD | 1590 | 7 | 0.0108 | 0.0615 | 0.0725 | 0.0829 | 0.3675 | 0.0484 | 1323 | ACSR/SD | 1.468 | 0.376 | 96.60 | 10,000 | 1791 | 42,600
FALCON/SD | 1590 | 13 | 0.0108 | 0.0607 | 0.0717 | 0.0818 | 0.3606 | 0.0512 | 1345 | ACSR/SD | 1.521 | 0.515 | 96.60 | 9,000 | 2039 | 55,100
CHUKAR/SD | 1780 | 8 | 0.0097 | 0.0554 | 0.0653 | 0.0810 | 0.3589 | 0.0519 | 1420 | ACSR/SD | 1.565 | 0.437 | 96.60 | 9,000 | 2068 | 51,100
BLUEBIRD/SD | 2156 | 8 | 0.0080 | 0.0470 | 0.0549 | 0.0783 | 0.3476 | 0.0570 | 1586 | ACSR/SD | 1.716 | 0.481 | 96.60 | 7,500 | 2504 | 60,700
| 503.6 | 12/7 | 0.0362 |  | 0.0441 | 0.5096 | 0.082 | 0.0262 | 646 | ACAR | 0.1628 | 0.1628 | 0.1628 | 0.316 |  | 11900
| 653.1 | 12/7 | 0.0279 |  | 0.0342 | 0.5097 | 0.0804 | 0.0302 | 760 | ACAR | 0.1854 | 0.1854 | 0.1854 | 0.325 |  | 15400
| 739.8 | 30/7 | 0.0240 |  | 0.0296 | 0.4994 | 0.0807 | 0.0298 | 831 | ACAR | 0.1414 | 0.1414 | 0.1414 | 0.354 |  | 15300
| 739.8 | 18/19 | 0.0252 |  | 0.0308 | 0.4882 | 0.0789 | 0.0344 | 814 | ACAR | 0.1414 | 0.1414 | 0.1414 | 0.398 |  | 18800
| 853.7 | 30/7 | 0.0208 |  | 0.0257 | 0.4882 | 0.0774 | 0.0344 | 907 | ACAR | 0.1519 | 0.1519 | 0.1519 | 0.447 |  | 17500
| 853.7 | 18/19 | 0.0218 |  | 0.0268 | 0.4817 | 0.0774 | 0.0359 | 890 | ACAR | 0.1519 | 0.1519 | 0.1519 | 0.502 |  | 21500
| 927.2 | 30/7 | 0.0192 |  | 0.0238 | 0.4739 | 0.0765 | 0.0377 | 955 | ACAR | 0.1583 | 0.1583 | 0.1583 | 0.563 |  | 19000
| 927.2 | 18/19 | 0.0201 |  | 0.0247 | 0.4739 | 0.0753 | 0.0377 | 936 | ACAR | 0.1583 | 0.1583 | 0.1583 | 0.609 |  | 23400
| 1024.5 | 30/7 | 0.0173 |  | 0.0216 | 0.4697 | 0.0753 | 0.0387 | 1015 | ACAR | 0.1664 | 0.1664 | 0.1664 | 0.642 |  | 20900
| 1024.5 | 18/19 | 0.0182 |  | 0.0225 | 0.4697 | 0.0747 | 0.039 | 995 | ACAR | 0.1664 | 0.1664 | 0.1664 | 0.680 |  | 25800
| 1081.0 | 30/7 | 0.0164 |  | 0.0205 | 0.4677 | 0.0745 | 0.0392 | 1048 | ACAR | 0.1709 | 0.1709 | 0.1709 | 0.684 |  | 22100
| 1081.0 | 18/19 | 0.0172 |  | 0.0213 | 0.4677 | 0.0744 | 0.0392 | 1028 | ACAR | 0.1709 | 0.1709 | 0.1709 | 0.720 |  | 27200
| 1109.0 | 30/7 | 0.0160 |  | 0.0200 | 0.4634 | 0.0744 | 0.0403 | 1065 | ACAR | 0.1731 | 0.1731 | 0.1731 | 0.741 |  | 22700
| 1109.0 | 18/19 | 0.0168 |  | 0.0208 | 0.4634 | 0.0738 | 0.0406 | 1044 | ACAR | 0.1731 | 0.1731 | 0.1731 | 0.743 |  | 27900
| 1172.0 | 30/7 | 0.0152 |  | 0.0190 | 0.4617 | 0.0736 | 0.0408 | 1101 | ACAR | 0.1780 | 0.1780 | 0.1780 | 0.772 |  | 24000
| 1172.0 | 18/19 | 0.0159 |  | 0.0198 | 0.4617 | 0.0735 | 0.0408 | 1080 | ACAR | 0.1780 | 0.1780 | 0.1780 | 0.783 |  | 29500
| 1197.0 | 30/7 | 0.0148 |  | 0.0187 | 0.4565 | 0.0735 | 0.0422 | 1115 | ACAR | 0.1799 | 0.1799 | 0.1799 | 0.806 |  | 24500
| 1197.0 | 18/19 | 0.0156 |  | 0.0194 | 0.4565 | 0.0727 | 0.0426 | 1094 | ACAR | 0.1799 | 0.1799 | 0.1799 | 0.814 |  | 30200
| 1280.0 | 30/7 | 0.0139 |  | 0.0175 | 0.4514 | 0.0725 | 0.0436 | 1160 | ACAR | 0.1860 | 0.1860 | 0.1860 | 0.846 |  | 26200
| 1280.0 | 18/19 | 0.0146 |  | 0.0182 | 0.4421 | 0.072 | 0.0467 | 1139 | ACAR | 0.1860 | 0.1860 | 0.1860 | 0.858 |  | 32200
| 1361.0 | 42/19 | 0.0133 |  | 0.0168 | 0.4339 | 0.0704 | 0.0492 | 1196 | ACAR | 0.1494 | 0.1494 | 0.1494 | 0.883 |  | 30300
| 1527.0 | 42/19 | 0.0118 |  | 0.0151 | 0.4297 | 0.0692 | 0.0505 | 1314 | ACAR | 0.1582 | 0.1582 | 0.1582 | 0.879 |  | 33600
| 1703.0 | 42/19 | 0.0106 |  | 0.0137 | 0.424 | 0.0686 | 0.0524 | 1363 | ACAR | 0.1671 | 0.1671 | 0.1671 | 0.914 |  | 37500
| 1933.0 | 42/19 | 0.00936 |  | 0.0123 | 0.4091 | 0.0678 | 0.0576 | 1465 | ACAR | 0.1780 | 0.1780 | 0.1780 | 0.927 |  | 42500
| 2267.0 | 42/19 | 0.00806 |  | 0.0108 | 0.4091 | 0.0656 | 0.0576 | 1594 | ACAR | 0.1928 | 0.1928 | 0.1928 | 0.953 |  | 49900
| 2493.0 | 72/19 | 0.00722 |  | 0.0099 | 0.404 | 0.0656 | 0.0598 | 1687 | ACAR | 0.1655 | 0.1655 | 0.1655 | 0.953 |  | 50400
| 2493.0 | 54/37 | 0.00743 |  | 0.0101 | 0.404 | 0.0647 | 0.0594 | 1670 | ACAR | 0.1655 | 0.1655 | 0.1655 | 0.966 |  | 57600
Swan/TP | #1 |  | 0.201 | 0.205 | 0.246 | 0.6605 | 0.100 | 0.0129 | 250 | ACSR/TP | 0.410 |  |  |  |  | 3720
Swanate/TP | #1 |  | 0.198 | 0.202 | 0.242 | 0.6562 | 0.0991 | 0.0134 | 255 | ACSR/TP | 0.421 |  |  |  |  | 4720
Swallow/TP | 1/0 |  | 0.160 | 0.163 | 0.195 | 0.6424 | 0.0973 | 0.0145 | 290 | ACSR/TP | 0.460 |  |  |  |  | 4590
Sparrow/TP | 2/0 |  | 0.126 | 0.129 | 0.154 | 0.6242 | 0.0947 | 0.0162 | 340 | ACSR/TP | 0.517 |  |  |  |  | 5700
Sparate/TP | 2/0 |  | 0.125 | 0.127 | 0.152 | 0.6197 | 0.0938 | 0.0169 | 345 | ACSR/TP | 0.532 |  |  |  |  | 7280
Robin/TP | 3/0 |  | 0.100 | 0.102 | 0.122 | 0.6061 | 0.0921 | 0.0182 | 395 | ACSR/TP | 0.580 |  |  |  |  | 7110
Raven/TP | 4/0 |  | 0.0794 | 0.0811 | 0.0970 | 0.5878 | 0.0893 | 0.0205 | 460 | ACSR/TP | 0.652 |  |  |  |  | 8760
Quail/TP | 266.2 |  | 0.0631 | 0.0644 | 0.0771 | 0.5698 | 0.0867 | 0.0230 | 535 | ACSR/TP | 0.731 |  |  |  |  | 10600
Pigeon/TP | 335.6 |  | 0.0500 | 0.0511 | 0.0612 | 0.5516 | 0.0841 | 0.0258 | 620 | ACSR/TP | 0.821 |  |  |  |  | 13200
Penguin/TP | 423.2 |  | 0.0397 | 0.0406 | 0.0485 | 0.5334 | 0.0814 | 0.0290 | 720 | ACSR/TP | 0.922 |  |  |  |  | 16700
Jaegar/TP | 456.4 |  | 0.0375 | 0.0385 | 0.0460 | 0.5335 | 0.0812 | 0.0292 | 740 | ACSR/TP | 0.922 |  |  |  |  | 12000
Waxwing/TP | 533.6 |  | 0.0321 | 0.0330 | 0.0394 | 0.5213 | 0.0795 | 0.0315 | 820 | ACSR/TP | 0.996 |  |  |  |  | 13800
Spoonbill/TP | 533.6 |  | 0.0319 | 0.0328 | 0.0392 | 0.5174 | 0.0786 | 0.0327 | 830 | ACSR/TP | 1.021 |  |  |  |  | 17400
Scaup/TP | 533.6 |  | 0.0318 | 0.0326 | 0.0390 | 0.5153 | 0.0782 | 0.0333 | 835 | ACSR/TP | 1.035 |  |  |  |  | 20000
Partridge/TP | 533.6 |  | 0.0317 | 0.0324 | 0.0388 | 0.5130 | 0.0778 | 0.0339 | 840 | ACSR/TP | 1.050 |  |  |  |  | 22600
Junco/TP | 533.6 |  | 0.0314 | 0.0321 | 0.0384 | 0.5086 | 0.0769 | 0.0352 | 855 | ACSR/TP | 1.081 |  |  |  |  | 27900
Ostrich/TP | 600.0 |  | 0.0282 | 0.0289 | 0.0345 | 0.5039 | 0.0764 | 0.0360 | 910 | ACSR/TP | 1.113 |  |  |  |  | 25400
Merlin/TP | 672.8 |  | 0.0254 | 0.0263 | 0.0313 | 0.5031 | 0.0768 | 0.0354 | 955 | ACSR/TP | 1.119 |  |  |  |  | 17400
Trogon/TP | 672.8 |  | 0.0254 | 0.0262 | 0.0313 | 0.5013 | 0.0763 | 0.0361 | 960 | ACSR/TP | 1.132 |  |  |  |  | 18900
Woodcock/TP | 672.8 |  | 0.0253 | 0.0260 | 0.0311 | 0.4992 | 0.0760 | 0.0367 | 965 | ACSR/TP | 1.147 |  |  |  |  | 21800
Widgeon/TP | 672.8 |  | 0.0252 | 0.0259 | 0.0310 | 0.4971 | 0.0755 | 0.0374 | 975 | ACSR/TP | 1.163 |  |  |  |  | 25000
Linnet/TP | 672.8 |  | 0.0251 | 0.0258 | 0.0308 | 0.4950 | 0.0751 | 0.0381 | 980 | ACSR/TP | 1.179 |  |  |  |  | 28200
Oriole/TP | 672.8 |  | 0.0249 | 0.0255 | 0.0305 | 0.4904 | 0.0743 | 0.0395 | 995 | ACSR/TP | 1.214 |  |  |  |  | 34700
Chickadee/TP | 795.0 |  | 0.0215 | 0.0223 | 0.0266 | 0.4901 | 0.0749 | 0.0385 | 1065 | ACSR/TP | 1.216 |  |  |  |  | 19900
Ptarmigan/TP | 795.0 |  | 0.0215 | 0.0223 | 0.0266 | 0.4881 | 0.0744 | 0.0392 | 1070 | ACSR/TP | 1.231 |  |  |  |  | 22100
Stork/TP | 795.0 |  | 0.0214 | 0.0221 | 0.0264 | 0.4862 | 0.0740 | 0.0399 | 1080 | ACSR/TP | 1.247 |  |  |  |  | 25700
Brant/TP | 795.0 |  | 0.0213 | 0.0220 | 0.0263 | 0.4840 | 0.0736 | 0.0407 | 1085 | ACSR/TP | 1.264 |  |  |  |  | 29300
Ibis/TP | 795.0 |  | 0.0213 | 0.0219 | 0.0261 | 0.4819 | 0.0732 | 0.0414 | 1095 | ACSR/TP | 1.281 |  |  |  |  | 32600
Lark/TP | 795.0 |  | 0.0211 | 0.0216 | 0.0259 | 0.4774 | 0.0723 | 0.0430 | 1110 | ACSR/TP | 1.319 |  |  |  |  | 40700
Pelican/TP | 954.0 |  | 0.0179 | 0.0187 | 0.0223 | 0.4758 | 0.0727 | 0.0422 | 1200 | ACSR/TP | 1.333 |  |  |  |  | 23500
Tailorbird/TP | 954.0 |  | 0.0180 | 0.0187 | 0.0222 | 0.4740 | 0.0724 | 0.0429 | 1205 | ACSR/TP | 1.348 |  |  |  |  | 26200
Toucan/TP | 954.0 |  | 0.0179 | 0.0186 | 0.0221 | 0.4719 | 0.0719 | 0.0437 | 1215 | ACSR/TP | 1.366 |  |  |  |  | 30400
Flicker/TP | 954.0 |  | 0.0178 | 0.0184 | 0.0220 | 0.4697 | 0.0715 | 0.0445 | 1225 | ACSR/TP | 1.385 |  |  |  |  | 34400
Hawk/TP | 954.0 |  | 0.0177 | 0.0183 | 0.0219 | 0.4676 | 0.0711 | 0.0454 | 1230 | ACSR/TP | 1.404 |  |  |  |  | 39000
Hen/TP | 954.0 |  | 0.0176 | 0.0181 | 0.0216 | 0.4631 | 0.0702 | 0.0471 | 1250 | ACSR/TP | 1.445 |  |  |  |  | 47600
Heron/TP | 1000.0 |  | 0.0168 | 0.0173 | 0.0206 | 0.4594 | 0.0697 | 0.0482 | 1290 | ACSR/TP | 1.479 |  |  |  |  | 50000
Nightingale/TP | 1034.0 |  | 0.0165 | 0.0174 | 0.0206 | 0.4695 | 0.0718 | 0.0439 | 1265 | ACSR/TP | 1.387 |  |  |  |  | 25400
Creeper/TP | 1034.0 |  | 0.0165 | 0.0173 | 0.0206 | 0.4676 | 0.0714 | 0.0447 | 1270 | ACSR/TP | 1.404 |  |  |  |  | 28400
Osprey/TP | 1113.0 |  | 0.0154 | 0.0162 | 0.0192 | 0.4637 | 0.0710 | 0.0456 | 1325 | ACSR/TP | 1.439 |  |  |  |  | 27400
Tody/TP | 1113.0 |  | 0.0154 | 0.0161 | 0.0192 | 0.4619 | 0.0706 | 0.0464 | 1330 | ACSR/TP | 1.456 |  |  |  |  | 30600
Sapsucker/TP | 1113.0 |  | 0.0153 | 0.0160 | 0.0190 | 0.4599 | 0.0702 | 0.0472 | 1340 | ACSR/TP | 1.475 |  |  |  |  | 35200
Parakeet/TP | 1113.0 |  | 0.0152 | 0.0159 | 0.0189 | 0.4577 | 0.0697 | 0.0481 | 1350 | ACSR/TP | 1.496 |  |  |  |  | 39600
Dove/TP | 1113.0 |  | 0.0152 | 0.0158 | 0.0188 | 0.4555 | 0.0693 | 0.0490 | 1360 | ACSR/TP | 1.517 |  |  |  |  | 45200
Eagle/TP | 1113.0 |  | 0.0151 | 0.0156 | 0.0185 | 0.4510 | 0.0685 | 0.0508 | 1385 | ACSR/TP | 1.561 |  |  |  |  | 55600
Kittiwake/TP | 1192.0 |  | 0.0144 | 0.0152 | 0.0180 | 0.4583 | 0.0702 | 0.0472 | 1385 | ACSR/TP | 1.490 |  |  |  |  | 29400
Skua/TP | 1210.0 |  | 0.0142 | 0.0149 | 0.0177 | 0.4553 | 0.0696 | 0.0484 | 1405 | ACSR/TP | 1.518 |  |  |  |  | 33200
Peacock/TP | 1210.0 |  | 0.0140 | 0.0147 | 0.0174 | 0.4511 | 0.0688 | 0.0502 | 1430 | ACSR/TP | 1.560 |  |  |  |  | 43200
Squab/TP | 1210.0 |  | 0.0140 | 0.0146 | 0.0173 | 0.4490 | 0.0683 | 0.0511 | 1440 | ACSR/TP | 1.581 |  |  |  |  | 48600
Wood/TP | 1210.0 |  | 0.0138 | 0.0144 | 0.0171 | 0.4445 | 0.0675 | 0.0530 | 1460 | ACSR/TP | 1.627 |  |  |  |  | 60000
Teal/TP | 1210.0 |  | 0.0139 | 0.0144 | 0.0171 | 0.4445 | 0.0675 | 0.0530 | 1460 | ACSR/TP | 1.627 |  |  |  |  | 27600
Swift/TP | 1272.0 |  | 0.0136 | 0.0146 | 0.0182 | 0.4548 | 0.0696 | 0.0483 | 1380 | ACSR/TP | 1.523 |  |  |  |  | 31400
Kingbird/TP | 1272.0 |  | 0.0134 | 0.0143 | 0.0169 | 0.4532 | 0.0695 | 0.0487 | 1440 | ACSR/TP | 1.539 |  |  |  |  | 34800
Turacos/TP | 1272.0 |  | 0.0135 | 0.0142 | 0.0169 | 0.4514 | 0.0690 | 0.0496 | 1450 | ACSR/TP | 1.556 |  |  |  |  | 45200
Rook/TP | 1272.0 |  | 0.0133 | 0.0140 | 0.0166 | 0.4472 | 0.0682 | 0.0514 | 1475 | ACSR/TP | 1.599 |  |  |  |  | 50400
Grosbeak/TP | 1272.0 |  | 0.0133 | 0.0139 | 0.0165 | 0.4450 | 0.0678 | 0.0524 | 1485 | ACSR/TP | 1.621 |  |  |  |  | 60800
Scoter/TP | 1272.0 |  | 0.0132 | 0.0137 | 0.0163 | 0.4405 | 0.0670 | 0.0543 | 1510 | ACSR/TP | 1.668 |  |  |  |  | 63000
Egret/TP | 1272.0 |  | 0.0132 | 0.0137 | 0.0163 | 0.4405 | 0.0669 | 0.0544 | 1510 | ACSR/TP | 1.669 |  |  |  |  | 36600
Siskin/TP | 1333.2 |  | 0.0128 | 0.0136 | 0.0161 | 0.4476 | 0.0685 | 0.0508 | 1495 | ACSR/TP | 1.594 |  |  |  |  | 47600
Flamingo/TP | 1333.2 |  | 0.0127 | 0.0134 | 0.0159 | 0.4435 | 0.0676 | 0.0527 | 1520 | ACSR/TP | 1.637 |  |  |  |  | 52800
Gannet/TP | 1333.2 |  | 0.0127 | 0.0133 | 0.0158 | 0.4414 | 0.0672 | 0.0536 | 1530 | ACSR/TP | 1.660 |  |  |  |  | 39200
Dunlin/TP | 1431.0 |  | 0.0120 | 0.0128 | 0.0151 | 0.4422 | 0.0677 | 0.0526 | 1565 | ACSR/TP | 1.651 |  |  |  |  | 51000
Stilt/TP | 1431.0 |  | 0.0119 | 0.0125 | 0.0148 | 0.4380 | 0.0668 | 0.0546 | 1590 | ACSR/TP | 1.696 |  |  |  |  | 56800
Starling/TP | 1431.0 |  | 0.0118 | 0.0124 | 0.0147 | 0.4358 | 0.0664 | 0.0556 | 1605 | ACSR/TP | 1.720 |  |  |  |  | 69200
Redwing/TP | 1431.0 |  | 0.0117 | 0.0122 | 0.0145 | 0.4314 | 0.0656 | 0.0576 | 1630 | ACSR/TP | 1.769 |  |  |  |  | 33400
Coot/TP | 1590.0 |  | 0.0108 | 0.0119 | 0.0148 | 0.4373 | 0.0671 | 0.0540 | 1590 | ACSR/TP | 1.703 |  |  |  |  | 40200
Macaw/TP | 1590.0 |  | 0.0108 | 0.0118 | 0.0147 | 0.4352 | 0.0666 | 0.0551 | 1600 | ACSR/TP | 1.727 |  |  |  |  | 43600
Turbit/TP | 1590.0 |  | 0.0108 | 0.0116 | 0.0137 | 0.4339 | 0.0665 | 0.0554 | 1670 | ACSR/TP | 1.741 |  |  |  |  | 44200
Tern/TP | 1590.0 |  | 0.0108 | 0.0117 | 0.0146 | 0.4339 | 0.0664 | 0.0557 | 1610 | ACSR/TP | 1.740 |  |  |  |  | 49600
Puffin/TP | 1590.0 |  | 0.0107 | 0.0115 | 0.0135 | 0.4319 | 0.0661 | 0.0564 | 1685 | ACSR/TP | 1.763 |  |  |  |  | 55800
Cuckoo/TP | 1590.0 |  | 0.0107 | 0.0113 | 0.0134 | 0.4298 | 0.0656 | 0.0575 | 1700 | ACSR/TP | 1.787 |  |  |  |  | 56400
Condor/TP | 1590.0 |  | 0.0107 | 0.0115 | 0.0143 | 0.4298 | 0.0656 | 0.0577 | 1640 | ACSR/TP | 1.787 |  |  |  |  | 63000
Drake/TP | 1590.0 |  | 0.0106 | 0.0112 | 0.0133 | 0.4275 | 0.0652 | 0.0586 | 1715 | ACSR/TP | 1.813 |  |  |  |  | 76800
Mallard/TP | 1590.0 |  | 0.0105 | 0.0111 | 0.0131 | 0.4230 | 0.0644 | 0.0608 | 1745 | ACSR/TP | 1.866 |  |  |  |  | 47400
Surfbird/TP | 1749.0 |  | 0.00979 | 0.0107 | 0.0125 | 0.4265 | 0.0654 | 0.0581 | 1775 | ACSR/TP | 1.825 |  |  |  |  | 48200
Turnstone/TP | 1800.0 |  | 0.00951 | 0.0104 | 0.0122 | 0.4242 | 0.0650 | 0.0590 | 1805 | ACSR/TP | 1.852 |  |  |  |  | 48800
Ruddy/TP | 1800.0 |  | 0.00956 | 0.0105 | 0.0130 | 0.4242 | 0.0649 | 0.0593 | 1745 | ACSR/TP | 1.852 |  |  |  |  | 63800
Canary/TP | 1800.0 |  | 0.00948 | 0.0103 | 0.0127 | 0.4200 | 0.0641 | 0.0614 | 1775 | ACSR/TP | 1.902 |  |  |  |  | 39600
Catbird/TP | 1908.0 |  | 0.00903 | 0.0102 | 0.0125 | 0.4231 | 0.0650 | 0.0592 | 1780 | ACSR/TP | 1.866 |  |  |  |  | 46800
Phoenix/TP | 1908.0 |  | 0.00904 | 0.0101 | 0.0124 | 0.4209 | 0.0645 | 0.0604 | 1795 | ACSR/TP | 1.891 |  |  |  |  | 51200
Corncrake/TP | 1908.0 |  | 0.00897 | 0.00987 | 0.0116 | 0.4196 | 0.0644 | 0.0607 | 1870 | ACSR/TP | 1.907 |  |  |  |  | 51800
Rail/TP | 1908.0 |  | 0.00902 | 0.00998 | 0.0123 | 0.4196 | 0.0643 | 0.0610 | 1810 | ACSR/TP | 1.907 |  |  |  |  | 57000
Towhee/TP | 1908.0 |  | 0.00899 | 0.00989 | 0.0122 | 0.4182 | 0.0640 | 0.0618 | 1820 | ACSR/TP | 1.924 |  |  |  |  | 67000
Redbird/TP | 1908.0 |  | 0.00889 | 0.00961 | 0.0113 | 0.4154 | 0.0635 | 0.0630 | 1910 | ACSR/TP | 1.958 |  |  |  |  | 67600
Cardinal/TP | 1908.0 |  | 0.00895 | 0.00973 | 0.0120 | 0.4155 | 0.0635 | 0.0632 | 1845 | ACSR/TP | 1.958 |  |  |  |  | 92200
Canvasback/TP | 1908.0 |  | 0.00879 | 0.00932 | 0.0110 | 0.4088 | 0.0623 | 0.0666 | 1965 | ACSR/TP | 2.043 |  |  |  |  | 50800
Snowbird/TP | 2067.0 |  | 0.00834 | 0.00941 | 0.0115 | 0.4146 | 0.0636 | 0.0628 | 1890 | ACSR/TP | 1.969 |  |  |  |  | 55400
Ortolan/TP | 2067.0 |  | 0.00833 | 0.00933 | 0.0114 | 0.4134 | 0.0634 | 0.0635 | 1900 | ACSR/TP | 1.984 |  |  |  |  | 61600
Whooper/TP | 2067.0 |  | 0.00831 | 0.00923 | 0.0113 | 0.4121 | 0.0631 | 0.0643 | 1915 | ACSR/TP | 2.001 |  |  |  |  | 73300
Curlew/TP | 2067.0 |  | 0.00826 | 0.00907 | 0.0112 | 0.4092 | 0.0625 | 0.0658 | 1940 | ACSR/TP | 2.038 |  |  |  |  | 54200
Avocet/TP | 2226.0 |  | 0.00774 | 0.00886 | 0.0108 | 0.4088 | 0.0627 | 0.0652 | 1975 | ACSR/TP | 2.043 |  |  |  |  | 59600
Bluejay/TP | 2226.0 |  | 0.00772 | 0.00876 | 0.0107 | 0.4075 | 0.0625 | 0.0659 | 1990 | ACSR/TP | 2.060 |  |  |  |  | 65600
Bullfinch/TP | 2226.0 |  | 0.00771 | 0.00867 | 0.0106 | 0.4062 | 0.0622 | 0.0667 | 2005 | ACSR/TP | 2.078 |  |  |  |  | 78200
Finch/TP | 2226.0 |  | 0.00767 | 0.00850 | 0.0104 | 0.4033 | 0.0617 | 0.0683 | 2035 | ACSR/TP | 2.116 |  |  |  |  | 78201
Swan/AW | #4 |  | 0.390 | 0.398 | 0.507 | 0.7148 | 0.1376 | 0.0025 | 150 | ACSR/AW | 0.250
Swanate/AW | #4 |  | 0.379 | 0.388 | 0.505 | 0.7105 | 0.1416 | 0.0021 | 150 | ACSR/AW | 0.257
Sparrow/AW | #2 |  | 0.245 | 0.250 | 0.327 | 0.6785 | 0.1276 | 0.0039 | 200 | ACSR/AW | 0.316
Sparate/AW | #2 |  | 0.238 | 0.244 | 0.327 | 0.6740 | 0.1293 | 0.0036 | 190 | ACSR/AW | 0.325
Robin/AW | #1 |  | 0.195 | 0.199 | 0.263 | 0.6603 | 0.1229 | 0.0048 | 235 | ACSR/AW | 0.354
Raven/AW | 1/0 |  | 0.154 | 0.157 | 0.211 | 0.6421 | 0.1181 | 0.0059 | 270 | ACSR/AW | 0.398
Quail/AW | 2/0 |  | 0.122 | 0.125 | 0.172 | 0.6240 | 0.1136 | 0.0071 | 310 | ACSR/AW | 0.447
Pigeon/AW | 3/0 |  | 0.0971 | 0.0991 | 0.139 | 0.6059 | 0.1095 | 0.0085 | 355 | ACSR/AW | 0.502
Penguin/AW | 4/0 |  | 0.0770 | 0.0786 | 0.112 | 0.5877 | 0.1057 | 0.0101 | 410 | ACSR/AW | 0.563
Waxwing/AW | 266.8 |  | 0.0635 | 0.0649 | 0.0777 | 0.5756 | 0.0905 | 0.0195 | 500 | ACSR/AW | 0.608
Spoonbill/AW | 266.8 |  | 0.0627 | 0.0641 | 0.0767 | 0.5717 | 0.0894 | 0.0204 | 510 | ACSR/AW | 0.624
Scaup/AW | 266.8 |  | 0.0622 | 0.0635 | 0.0760 | 0.5696 | 0.0889 | 0.0209 | 515 | ACSR/AW | 0.632
Partridge/AW | 266.8 |  | 0.0615 | 0.0628 | 0.0752 | 0.5673 | 0.0885 | 0.0213 | 520 | ACSR/AW | 0.642
Junco/AW | 266.8 |  | 0.0602 | 0.0615 | 0.0736 | 0.5629 | 0.0875 | 0.0222 | 530 | ACSR/AW | 0.660
Ostrich/AW | 300.0 |  | 0.0547 | 0.0559 | 0.0669 | 0.5582 | 0.0871 | 0.0226 | 560 | ACSR/AW | 0.680
Merlin/AW | 336.4 |  | 0.0504 | 0.0515 | 0.0617 | 0.5574 | 0.0878 | 0.0219 | 585 | ACSR/AW | 0.684
Trogon/AW | 336.4 |  | 0.0502 | 0.0514 | 0.0615 | 0.5556 | 0.0873 | 0.0224 | 585 | ACSR/AW | 0.692
Woodcock/AW | 336.4 |  | 0.0497 | 0.0509 | 0.0608 | 0.5535 | 0.0868 | 0.0229 | 590 | ACSR/AW | 0.701
Widgeon/AW | 336.4 |  | 0.0493 | 0.0504 | 0.0603 | 0.5514 | 0.0863 | 0.0234 | 595 | ACSR/AW | 0.710
Linnet/AW | 336.4 |  | 0.0488 | 0.0499 | 0.0597 | 0.5493 | 0.0858 | 0.0239 | 605 | ACSR/AW | 0.720
Oriole/AW | 336.4 |  | 0.0478 | 0.0488 | 0.0584 | 0.5447 | 0.0848 | 0.0250 | 615 | ACSR/AW | 0.741
Chickadee/AW | 397.5 |  | 0.0426 | 0.0437 | 0.0522 | 0.5443 | 0.0858 | 0.0239 | 650 | ACSR/AW | 0.743
Ptarmigan/AW | 397.5 |  | 0.0425 | 0.0435 | 0.0521 | 0.5424 | 0.0853 | 0.0244 | 655 | ACSR/AW | 0.752
Stork/AW | 397.5 |  | 0.0421 | 0.0431 | 0.0516 | 0.5404 | 0.0849 | 0.0249 | 660 | ACSR/AW | 0.762
Brant/AW | 397.5 |  | 0.0417 | 0.0427 | 0.0510 | 0.5383 | 0.0843 | 0.0255 | 665 | ACSR/AW | 0.772
Ibis/AW | 397.5 |  | 0.0413 | 0.0423 | 0.0506 | 0.5362 | 0.0839 | 0.0260 | 670 | ACSR/AW | 0.783
Lark/AW | 397.5 |  | 0.0404 | 0.0414 | 0.0494 | 0.5317 | 0.0829 | 0.0271 | 685 | ACSR/AW | 0.806
Pelican/AW | 477.0 |  | 0.0355 | 0.0365 | 0.0436 | 0.5300 | 0.0838 | 0.0261 | 735 | ACSR/AW | 0.814
Tailorbird/AW | 477.0 |  | 0.0354 | 0.0364 | 0.0435 | 0.5282 | 0.0833 | 0.0267 | 735 | ACSR/AW | 0.823
Toucan/AW | 477.0 |  | 0.0351 | 0.0360 | 0.0430 | 0.5262 | 0.0828 | 0.0273 | 745 | ACSR/AW | 0.834
Flicker/AW | 477.0 |  | 0.0347 | 0.0356 | 0.0426 | 0.5240 | 0.0823 | 0.0279 | 750 | ACSR/AW | 0.846
Hawk/AW | 477.0 |  | 0.0344 | 0.0353 | 0.0422 | 0.5219 | 0.0818 | 0.0285 | 755 | ACSR/AW | 0.858
Hen/AW | 477.0 |  | 0.0337 | 0.0345 | 0.0412 | 0.5174 | 0.0808 | 0.0297 | 775 | ACSR/AW | 0.883
Heron/AW | 500.0 |  | 0.0321 | 0.0329 | 0.0393 | 0.5137 | 0.0803 | 0.0304 | 795 | ACSR/AW | 0.904
Osprey/AW | 556.5 |  | 0.0304 | 0.0313 | 0.0374 | 0.5180 | 0.0820 | 0.0282 | 810 | ACSR/AW | 0.879
Tody/AW | 556.5 |  | 0.0304 | 0.0312 | 0.0373 | 0.5162 | 0.0814 | 0.0289 | 815 | ACSR/AW | 0.890
Sapsucker/AW | 556.5 |  | 0.0301 | 0.0309 | 0.0369 | 0.5142 | 0.0810 | 0.0295 | 820 | ACSR/AW | 0.901
Parakeet/AW | 556.5 |  | 0.0298 | 0.0306 | 0.0365 | 0.5119 | 0.0804 | 0.0302 | 830 | ACSR/AW | 0.914
Dove/AW | 556.5 |  | 0.0295 | 0.0303 | 0.0362 | 0.5098 | 0.0800 | 0.0308 | 840 | ACSR/AW | 0.927
Eagle/AW | 556.5 |  | 0.0289 | 0.0296 | 0.0354 | 0.5053 | 0.0790 | 0.0321 | 855 | ACSR/AW | 0.953
Peacock/AW | 605.0 |  | 0.0274 | 0.0282 | 0.0336 | 0.5054 | 0.0795 | 0.0314 | 875 | ACSR/AW | 0.953
Squab/AW | 605.0 |  | 0.0271 | 0.0279 | 0.0333 | 0.5033 | 0.0790 | 0.0321 | 885 | ACSR/AW | 0.966
Wood_Duck/AW | 605.0 |  | 0.0266 | 0.0273 | 0.0326 | 0.4988 | 0.0780 | 0.0335 | 905 | ACSR/AW | 0.994
Teal/AW | 605.0 |  | 0.0266 | 0.0273 | 0.0326 | 0.4988 | 0.0780 | 0.0335 | 900 | ACSR/AW | 0.994
Swift/AW | 636.0 |  | 0.0270 | 0.0280 | 0.0347 | 0.5091 | 0.0806 | 0.0300 | 855 | ACSR/AW | 0.930
Kingbird/AW | 636.0 |  | 0.0266 | 0.0275 | 0.0328 | 0.5075 | 0.0804 | 0.0302 | 885 | ACSR/AW | 0.940
Turacos/AW | 636.0 |  | 0.0266 | 0.0274 | 0.0327 | 0.5057 | 0.0799 | 0.0309 | 890 | ACSR/AW | 0.951
Goldfinch/AW | 636.0 |  | 0.0263 | 0.0271 | 0.0324 | 0.5037 | 0.0795 | 0.0315 | 895 | ACSR/AW | 0.963
Rook/AW | 636.0 |  | 0.0261 | 0.0268 | 0.0320 | 0.5015 | 0.0790 | 0.0322 | 905 | ACSR/AW | 0.977
Grosbeak/AW | 636.0 |  | 0.0258 | 0.0265 | 0.0317 | 0.4993 | 0.0785 | 0.0329 | 915 | ACSR/AW | 0.990
Scoter/AW | 636.0 |  | 0.0253 | 0.0260 | 0.0310 | 0.4948 | 0.0775 | 0.0343 | 935 | ACSR/AW | 1.019
Egret/AW | 636.0 |  | 0.0253 | 0.0260 | 0.0311 | 0.4948 | 0.0774 | 0.0344 | 930 | ACSR/AW | 1.019
Flamingo/AW | 666.6 |  | 0.0249 | 0.0256 | 0.0306 | 0.4978 | 0.0784 | 0.0330 | 935 | ACSR/AW | 1.000
Gannet/AW | 666.6 |  | 0.0246 | 0.0254 | 0.0303 | 0.4956 | 0.0779 | 0.0337 | 940 | ACSR/AW | 1.014
Stilt/AW | 715.5 |  | 0.0232 | 0.0239 | 0.0285 | 0.4923 | 0.0776 | 0.0342 | 980 | ACSR/AW | 1.036
Starling/AW | 715.5 |  | 0.0229 | 0.0236 | 0.0282 | 0.4901 | 0.0771 | 0.0349 | 985 | ACSR/AW | 1.051
Redwing/AW | 715.5 |  | 0.0225 | 0.0232 | 0.0277 | 0.4857 | 0.0761 | 0.0364 | 1005 | ACSR/AW | 1.081
Coot/AW | 795.0 |  | 0.0216 | 0.0226 | 0.0278 | 0.4916 | 0.0780 | 0.0336 | 990 | ACSR/AW | 1.040
Macaw/AW | 795.0 |  | 0.0215 | 0.0224 | 0.0277 | 0.4895 | 0.0774 | 0.0344 | 995 | ACSR/AW | 1.055
Turbit/AW | 795.0 |  | 0.0213 | 0.0220 | 0.0263 | 0.4882 | 0.0774 | 0.0345 | 1025 | ACSR/AW | 1.063
Tern/AW | 795.0 |  | 0.0214 | 0.0223 | 0.0275 | 0.4882 | 0.0771 | 0.0349 | 1000 | ACSR/AW | 1.063
Puffin/AW | 795.0 |  | 0.0210 | 0.0218 | 0.0260 | 0.4862 | 0.0768 | 0.0353 | 1035 | ACSR/AW | 1.077
Cuckoo/AW | 795.0 |  | 0.0209 | 0.0216 | 0.0257 | 0.4840 | 0.0764 | 0.0360 | 1045 | ACSR/AW | 1.092
Condor/AW | 795.0 |  | 0.0210 | 0.0218 | 0.0270 | 0.4841 | 0.0762 | 0.0363 | 1020 | ACSR/AW | 1.092
Drake/AW | 795.0 |  | 0.0206 | 0.0213 | 0.0254 | 0.4818 | 0.0759 | 0.0368 | 1055 | ACSR/AW | 1.108
Mallard/AW | 795.0 |  | 0.0203 | 0.0209 | 0.0249 | 0.4773 | 0.0749 | 0.0384 | 1080 | ACSR/AW | 1.140

## Cables
Code | AWG | Stranding | Insulation Thickness (inches) | AWG -neutral | Strands - neutral | Breaking strength (lbs) | Outside Diameter conductor (inches) | Diameter - cable (inches) | XLP (lbs/kft) | POLY (lbs/kft) | Ampacity - XLP | Ampacity - POLY | Type
Pekingese | 6 | Solid | 0.045 | 6 | 7 | 563 | 0.44 |  | 64 | 62 | 85 | 70 | DOAC - service drop
Collie | 6 | 7 | 0.045 | 6 | 7 | 563 | 0.46 |  | 69 | 63 | 85 | 70 | DOAC - service drop
Dachshund | 4 | Solid | 0.045 | 4 | 7 | 881 | 0.53 |  | 96 | 93 | 115 | 90 | DOAC - service drop
Spaniel | 4 | 7 | 0.045 | 4 | 7 | 881 | 0.56 |  | 101 | 95 | 115 | 90 | DOAC - service drop
Doberman | 2 | 7 | 0.045 | 2 | 7 | 1350 | 0.68 |  | 153 | 146 | 150 | 120 | DOAC - service drop
Malamute | 1/0 | 19 | 0.060 | 1/0 | 7 | 1990 | 0.87 |  | 243 | 234 | 205 | 160 | DOAC - service drop
Setter | 6 | Solid | 0.045 | 6 | 6/1 | 1190 | 0.46 |  | 75 | 73 | 85 | 70 | DOAC - service drop
Shepherd | 6 | 7 | 0.045 | 6 | 6/1 | 1190 | 0.48 |  | 78 | 75 | 85 | 70 | DOAC - service drop
Eskimo | 4 | Solid | 0.045 | 4 | 6/1 | 1860 | 0.55 |  | 114 | 112 | 115 | 90 | DOAC - service drop
Terrier | 4 | 7 | 0.045 | 4 | 6/1 | 1860 | 0.58 |  | 119 | 114 | 115 | 90 | DOAC - service drop
Chow | 2 | 7 | 0.045 | 2 | 6/1 | 2850 | 0.70 |  | 182 | 175 | 150 | 120 | DOAC - service drop
Bull | 1/0 | 19 | 0.060 | 1/0 | 6/1 | 4380 | 0.90 |  | 289 | 280 | 205 | 160 | DOAC - service drop
Chihuahua | 6 | Solid | 0.045 | 6 | 7 | 1110 | 0.46 |  | 68 | 66 | 85 | 70 | DOAC - service drop
Vizsla | 6 | 7 | 0.045 | 6 | 7 | 1110 | 0.48 |  | 71 | 67 | 85 | 70 | DOAC - service drop
Harrier | 4 | Solid | 0.045 | 4 | 7 | 1760 | 0.55 |  | 102 | 100 | 115 | 90 | DOAC - service drop
Whippet | 4 | 7 | 0.045 | 4 | 7 | 1760 | 0.58 |  | 107 | 102 | 115 | 90 | DOAC - service drop
Schnauzer | 2 | 7 | 0.045 | 2 | 7 | 2800 | 0.70 |  | 163 | 156 | 150 | 120 | DOAC - service drop
Heeler | 1/0 | 19 | 0.060 | 1/0 | 7 | 4460 | 0.90 |  | 1259 | 251 | 205 | 160 | DOAC - service drop
Minex | 6 | Solid | 0.045 | 6 | 7 | 1110 | 0.53 |  | 107 | 103 | 85 | 70 | TOAC - service drop
Hippa | 6 | 7 | 0.045 | 6 | 7 | 1110 | 0.57 |  | 107 | 106 | 85 | 70 | TOAC - service drop
Prawn | 4 | Solid | 0.045 | 4 | 7 | 1760 | 0.62 |  | 158 | 154 | 115 | 90 | TOAC - service drop
Barnacles | 4 | 7 | 0.045 | 4 | 7 | 1760 | 0.67 |  | 160 | 157 | 115 | 90 | TOAC - service drop
Shrimp | 2 | 7 | 0.045 | 2 | 7 | 2800 | 0.80 |  | 243 | 238 | 150 | 120 | TOAC - service drop
Gammarus | 1/0 | 7 | 0.060 | 1/0 | 7 | 4460 | 1.02 |  | 390 | 384 | 205 | 160 | TOAC - service drop
Leda | 1/0 | 19 | 0.060 | 1/0 | 7 | 4460 | 1.03 |  | 384 | 378 | 205 | 160 | TOAC - service drop
Dungeness | 2/0 | 7 | 0.060 | 2/0 | 7 | 5390 | 1.11 |  | 481 | 474 | 235 | 185 | TOAC - service drop
Cyclops | 2/0 | 19 | 0.060 | 2/0 | 7 | 5390 | 1.12 |  | 473 | 467 | 235 | 185 | TOAC - service drop
Flustra | 3/0 | 19 | 0.060 | 3/0 | 7 | 6790 | 1.23 |  | 596 | 589 | 275 | 215 | TOAC - service drop
Lepas | 4/0 | 19 | 0.060 | 4/0 | 7 | 8560 | 1.35 |  | 725 | 716 | 315 | 245 | TOAC - service drop
Artemia | 4 | Solid | 0.045 | 6 | 7 | 1110 | 0.62 |  | 134 | 132 | 115 | 90 | TOAC - service drop
Crab | 4 | 7 | 0.045 | 6 | 7 | 1110 | 0.67 |  | 144 | 141 | 115 | 90 | TOAC - service drop
Solaster | 2 | 7 | 0.045 | 4 | 7 | 1760 | 0.80 |  | 216 | 212 | 150 | 120 | TOAC - service drop
Sandcrab | 1/0 | 7 | 0.060 | 2 | 7 | 2800 | 1.02 |  | 348 | 341 | 205 | 160 | TOAC - service drop
Echinus | 1/0 | 19 | 0.060 | 2 | 7 | 2800 | 1.03 |  | 342 | 336 | 205 | 160 | TOAC - service drop
Crayfish | 2/0 | 7 | 0.060 | 1 | 7 | 3530 | 1.11 |  | 453 | 423 | 235 | 185 | TOAC - service drop
Sipho | 2/0 | 19 | 0.060 | 1 | 7 | 3530 | 1.12 |  | 441 | 423 | 235 | 185 | TOAC - service drop
Fulgar | 3/0 | 19 | 0.060 | 1/0 | 7 | 4460 | 1.23 |  | 525 | 518 | 275 | 215 | TOAC - service drop
Arca | 4/0 | 19 | 0.060 | 2/0 | 7 | 5390 | 1.35 |  | 640 | 632 | 315 | 245 | TOAC - service drop
Haiotis | 6 | Solid | 0.045 | 6 | 7 | 563 | 0.53 |  | 103 | 99 | 85 | 70 | TOAC - service drop
Patella | 6 | 7 | 0.045 | 6 | 7 | 563 | 0.57 |  | 104 | 102 | 85 | 70 | TOAC - service drop
Fusus | 4 | Solid | 0.045 | 4 | 7 | 881 | 0.62 |  | 152 | 148 | 115 | 90 | TOAC - service drop
Oyster | 4 | 7 | 0.045 | 4 | 7 | 881 | 0.67 |  | 154 | 152 | 115 | 90 | TOAC - service drop
Mussel | 2 | 7 | 0.045 | 4 | 7 | 881 | 0.80 |  | 208 | 204 | 150 | 120 | TOAC - service drop
Clam | 2 | 7 | 0.045 | 2 | 7 | 1350 | 0.80 |  | 232 | 228 | 150 | 120 | TOAC - service drop
Snail | 1/0 | 7 | 0.060 | 2 | 7 | 1350 | 1.02 |  | 336 | 329 | 205 | 160 | TOAC - service drop
Murex | 1/0 | 7 | 0.060 | 1/0 | 7 | 1990 | 1.02 |  | 374 | 367 | 205 | 160 | TOAC - service drop
Purpura | 1/0 | 19 | 0.060 | 1/0 | 7 | 1990 | 1.03 |  | 368 | 362 | 205 | 160 | TOAC - service drop
Nassa | 2/0 | 7 | 0.060 | 2/0 | 7 | 2510 | 1.11 |  | 461 | 453 | 235 | 185 | TOAC - service drop
Melita | 3/0 | 19 | 0.060 | 3/0 | 19 | 3310 | 1.23 |  | 585 | 563 | 275 | 215 | TOAC - service drop
Portunus | 4/0 | 19 | 0.060 | 4/0 | 19 | 4020 | 1.35 |  | 693 | 684 | 315 | 245 | TOAC - service drop
Nannynose | 336.4 | 19 | 0.080 | 336.4 | 19 | 6146 | 1.72 |  | 1110 | 1096 | 420 | 325 | TOAC - service drop
Paludina | 6 | Solid | 0.045 | 6 | 6/1 | 1190 | 0.53 |  | 114 | 113 | 85 | 70 | TOAC - service drop
Voluta | 6 | 7 | 0.045 | 6 | 6/1 | 1190 | 0.57 |  | 115 | 112 | 85 | 70 | TOAC - service drop
Whelk | 4 | Solid | 0.045 | 4 | 6/1 | 1860 | 0.62 |  | 163 | 161 | 115 | 90 | TOAC - service drop
Periwinkle | 4 | 7 | 0.045 | 4 | 6/1 | 1860 | 0.67 |  | 172 | 169 | 115 | 90 | TOAC - service drop
Conch | 2 | 7 | 0.045 | 2 | 6/1 | 2850 | 0.80 |  | 262 | 257 | 150 | 120 | TOAC - service drop
Neritina | 1/0 | 7 | 0.060 | 1/0 | 6/1 | 4380 | 1.02 |  | 420 | 414 | 205 | 160 | TOAC - service drop
Cenia | 1/0 | 19 | 0.060 | 1/0 | 6/1 | 4380 | 1.03 |  | 414 | 408 | 205 | 160 | TOAC - service drop
Runcina | 2/0 | 7 | 0.060 | 2/0 | 6/1 | 5310 | 1.11 |  | 519 | 512 | 235 | 185 | TOAC - service drop
Triton | 2/0 | 19 | 0.060 | 2/0 | 6/1 | 5310 | 1.12 |  | 511 | 505 | 235 | 185 | TOAC - service drop
Cherrystone | 3/0 | 7 | 0.060 | 3/0 | 6/1 | 6620 | 1.22 |  | 656 | 643 | 275 | 215 | TOAC - service drop
Mursia | 3/0 | 19 | 0.060 | 3/0 | 6/1 | 6620 | 1.23 |  | 633 | 626 | 275 | 215 | TOAC - service drop
Razor | 4/0 | 7 | 0.060 | 4/0 | 6/1 | 8350 | 1.34 |  | 814 | 799 | 315 | 245 | TOAC - service drop
Zuzara | 4/0 | 19 | 0.060 | 4/0 | 6/1 | 8350 | 1.35 |  | 785 | 777 | 315 | 245 | TOAC - service drop
Limpet | 336.4 | 19 | 0.080 | 336.4 | 18/1 | 8680 | 1.72 |  | 1161 | 1147 | 420 | 325 | TOAC - service drop
Scallop | 4 | Solid | 0.045 | 6 | 6/1 | 1190 | 0.62 |  | 142 | 139 | 115 | 90 | TOAC - service drop
Strombus | 4 | 7 | 0.045 | 6 | 6/1 | 1190 | 0.67 |  | 151 | 148 | 115 | 90 | TOAC - service drop
Cockle | 2 | 7 | 0.045 | 4 | 6/1 | 1860 | 0.80 |  | 228 | 224 | 150 | 120 | TOAC - service drop
Janthina | 1/0 | 7 | 0.060 | 2 | 6/1 | 2850 | 1.02 |  | 367 | 360 | 205 | 160 | TOAC - service drop
Ranella | 1/0 | 19 | 0.060 | 2 | 6/1 | 2850 | 1.03 |  | 361 | 356 | 205 | 160 | TOAC - service drop
Cavolinia | 2/0 | 7 | 0.060 | 1 | 6/1 | 3550 | 1.11 |  | 452 | 444 | 235 | 185 | TOAC - service drop
Clio | 2/0 | 19 | 0.060 | 1 | 6/1 | 3550 | 1.12 |  | 444 | 437 | 235 | 185 | TOAC - service drop
Sanddollar | 3/0 | 7 | 0.060 | 1/0 | 6/1 | 4380 | 1.22 |  | 570 | 557 | 275 | 215 | TOAC - service drop
Aega | 3/0 | 19 | 0.060 | 1/0 | 6/1 | 4380 | 1.23 |  | 565 | 552 | 275 | 215 | TOAC - service drop
Cuttlefish | 4/0 | 7 | 0.060 | 2/0 | 6/1 | 5310 | 1.33 |  | 706 | 691 | 315 | 245 | TOAC - service drop
Cerapus | 4/0 | 19 | 0.060 | 2/0 | 6/1 | 5310 | 1.35 |  | 678 | 670 | 315 | 245 | TOAC - service drop
Cowry | 336.4 | 19 | 0.080 | 4/0 | 6/1 | 8350 | 1.72 |  | 1135 | 1093 | 420 | 325 | TOAC - service drop
Clydesdale | 4 | Solid | 0.045 | 4 | 7 | 881 | 0.68 |  | 208 | 201 | 100 | 80 | QOAC - service drop
Pinto | 4 | 7/w | 0.045 | 4 | 7 | 881 | 0.73 |  | 223 | 207 | 100 | 80 | QOAC - service drop
Mustang | 2 | 7/w | 0.045 | 2 | 7 | 1350 | 0.88 |  | 333 | 312 | 135 | 105 | QOAC - service drop
Criollo | 1/0 | 19/w | 0.060 | 1/0 | 7 | 1990 | 1.12 |  | 529 | 504 | 180 | 140 | QOAC - service drop
Percheron | 2/0 | 19/w | 0.060 | 2/0 | 7 | 2510 | 1.24 |  | 649 | 620 | 205 | 160 | QOAC - service drop
Hanoverian | 3/0 | 19/w | 0.060 | 3/0 | 19 | 3310 | 1.36 |  | 799 | 765 | 235 | 185 | QOAC - service drop
Oldenburg | 4/0 | 19/w | 0.060 | 4/0 | 19 | 4020 | 1.50 |  | 986 | 946 | 275 | 210 | QOAC - service drop
Lippizaner | 336.4 | 19/w | 0.080 | 336.4 | 19 | 6146 | 1.91 |  | 1546 | 1519 | 370 | 280 | QOAC - service drop
Morochuca | 6 | Solid | 0.045 | 6 | 6/1 | 1190 | 0.58 |  | 152 | 147 | 75 | 60 | QOAC - service drop
Chola | 6 | 7/W | 0.045 | 6 | 6/1 | 1190 | 0.62 |  | 162 | 151 | 75 | 60 | QOAC - service drop
Morgan | 4 | Solid | 0.045 | 4 | 6/1 | 1860 | 0.69 |  | 226 | 220 | 100 | 80 | QOAC - service drop
Hackney | 4 | 7/W | 0.045 | 4 | 6/1 | 1860 | 0.74 |  | 241 | 226 | 100 | 80 | QOAC - service drop
Palomino | 2 | 7/W | 0.045 | 2 | 6/1 | 2850 | 0.89 |  | 362 | 342 | 135 | 105 | QOAC - service drop
Costena | 1/0 | 19/W | 0.060 | 1/0 | 6/1 | 4380 | 1.14 |  | 575 | 550 | 180 | 140 | QOAC - service drop
Grullo | 2/0 | 19/W | 0.060 | 2/0 | 6/1 | 5310 | 1.26 |  | 707 | 678 | 205 | 160 | QOAC - service drop
Suffolk | 3/0 | 19/W | 0.060 | 3/0 | 6/1 | 6620 | 1.38 |  | 872 | 838 | 235 | 180 | QOAC - service drop
Appaloosa | 4/0 | 19/W | 0.060 | 4/0 | 6/1 | 8350 | 1.52 |  | 1079 | 1039 | 275 | 210 | QOAC - service drop
Bronco | 336.4 | 19/W | 0.080 | 336.4 | 18/1 | 8580 | 1.92 |  | 1613 | 1568 | 370 | 280 | QOAC - service drop
Gelding | 336.4 | 19/W | 0.080 | 4/0 | 6/1 | 8350 | 1.85 |  | 1548 | 1494 | 370 | 280 | QOAC - service drop
Hurricane | 500 | 37/w | 0.080 | 336.4 | 26/7 | 14100 | 2.21 |  | 2196 | 2186 | 480 | 360 | QOAC - service drop
Bay | 6 | Solid | 0.045 | 6 | 7 | 1110 | 0.59 |  | 145 | 140 | 75 | 60 | QOAC - service drop
French-Coach | 6 | 7/w | 0.045 | 6 | 7 | 1110 | 0.63 |  | 155 | 144 | 75 | 60 | QOAC - service drop
German-Coach | 4 | Solid | 0.045 | 4 | 7 | 1760 | 0.69 |  | 214 | 208 | 100 | 80 | QOAC - service drop
Arabian | 4 | 7/w | 0.045 | 4 | 7 | 1760 | 0.74 |  | 229 | 214 | 100 | 80 | QOAC - service drop
Belgian | 2 | 7/w | 0.045 | 2 | 7 | 2800 | 0.89 |  | 344 | 323 | 135 | 105 | QOAC - service drop
Shetland | 1/0 | 19/w | 0.060 | 1/0 | 7 | 4460 | 1.14 |  | 546 | 521 | 180 | 140 | QOAC - service drop
Thoroughbred | 2/0 | 19/w | 0.060 | 2/0 | 7 | 5390 | 1.26 |  | 670 | 641 | 205 | 160 | QOAC - service drop
Trotter | 3/0 | 19/w | 0.060 | 3/0 | 7 | 6790 | 1.38 |  | 825 | 791 | 135 | 185 | QOAC - service drop
Walking | 4/0 | 19/w | 0.060 | 4/0 | 7 | 8560 | 1.52 |  | 1019 | 979 | 275 | 210 | QOAC - service drop
Walnut | 6 | 6/1 | 0.030 |  |  |  | 0.26 |  | 1131 | 49 | 47 | 105 | SOAC - service drop
Butternut | 4 | 6/1 | 0.030 |  |  |  | 0.30 |  | 1760 | 72 | 70 | 135 | SOAC - service drop
Hickory | 4 | 7/1 | 0.030 |  |  |  | 0.31 |  | 2240 | 82 | 80 | 135 | SOAC - service drop
Pignut | 2 | 6/1 | 0.045 |  |  |  | 0.40 |  | 2710 | 118 | 115 | 180 | SOAC - service drop
Beech | 2 | 7/1 | 0.045 |  |  |  | 0.41 |  | 3460 | 134 | 131 | 180 | SOAC - service drop
Chestnut | 1 | 6/1 | 0.045 |  |  |  | 0.43 |  | 3370 | 146 | 142 | 210 | SOAC - service drop
Almond | 1/0 | 6/1 | 0.060 |  |  |  | 0.51 |  | 4160 | 190 | 185 | 235 | SOAC - service drop
Pecan | 2/0 | 6/1 | 0.060 |  |  |  | 0.55 |  | 5040 | 234 | 228 | 270 | SOAC - service drop
Filbert | 3/0 | 6/1 | 0.060 |  |  |  | 0.61 |  | 6290 | 289 | 281 | 305 | SOAC - service drop
Buckeye | 4/0 | 6/1 | 0.060 |  |  |  | 0.67 |  | 7930 | 366 | 349 | 345 | SOAC - service drop
Hackberry | 266.8 | 18/1 | 0.060 |  |  |  | 0.71 |  | 6540 | 355 | 347 | 435 | SOAC - service drop
Apple | 6 | Solid | 0.030 |  |  |  | 0.22 |  | 445 | 33 | 32 | 105 | SOAC - service drop
Pear | 4 | Solid | 0.030 |  |  |  | 0.26 |  | 675 | 49 | 47 | 135 | SOAC - service drop
Apricot | 4 | 7 | 0.030 |  |  |  | 0.29 |  | 790 | 52 | 51 | 140 | SOAC - service drop
Peach | 2 | 7 | 0.045 |  |  |  | 0.37 |  | 1220 | 87 | 84 | 180 | SOAC - service drop
Quince | 1/0 | 7 | 0.060 |  |  |  | 0.48 |  | 1790 | 141 | 136 | 240 | SOAC - service drop
Orange | 2/0 | 7 | 0.060 |  |  |  | 0.52 |  | 2260 | 172 | 166 | 280 | SOAC - service drop
Fig | 3/0 | 7 | 0.060 |  |  |  | 0.57 |  | 2740 | 211 | 204 | 320 | SOAC - service drop
Olive | 4/0 | 7 | 0.060 |  |  |  | 0.63 |  | 3450 | 259 | 251 | 370 | SOAC - service drop
Mulberry | 266.8 | 19 | 0.060 |  |  |  | 0.69 |  | 4470 | 314 | 306 | 430 | SOAC - service drop
Anona | 336.4 | 19 | 0.060 |  |  |  | 0.77 |  | 5535 | 388 | 379 | 495 | SOAC - service drop
Huckleberry | 477 | 37 | 0.080 |  |  |  | 0.93 |  | 7820 | 550 | 538 | 610 | SOAC - service drop
Paw_Paw | 556.5 | 37 | 0.080 |  |  |  | 0.99 |  | 8950 | 633 | 619 | 670 | SOAC - service drop
Princeton | 6 |  | 0.060 |  |  |  | 0.31 |  | 44 |  | 65 |  | single conductor - 600v
Mercer | 4 |  | 0.060 |  |  |  | 0.36 |  | 63 |  | 85 |  | single conductor - 600v
Clemson | 2 |  | 0.060 |  |  |  | 0.42 |  | 92 |  | 115 |  | single conductor - 600v
Kenyon | 1 |  | 0.080 |  |  |  | 0.50 |  | 121 |  | 130 |  | single conductor - 600v
Harvard | 1/0 |  | 0.080 |  |  |  | 0.54 |  | 146 |  | 150 |  | single conductor - 600v
Yale | 2/0 |  | 0.080 |  |  |  | 0.59 |  | 177 |  | 170 |  | single conductor - 600v
Tufts | 3/0 |  | 0.080 |  |  |  | 0.64 |  | 215 |  | 195 |  | single conductor - 600v
Beloit | 4/0 |  | 0.080 |  |  |  | 0.70 |  | 263 |  | 225 |  | single conductor - 600v
Hofstra | 250 |  | 0.095 |  |  |  | 0.77 |  | 314 |  | 250 |  | single conductor - 600v
Gonzaga | 300 |  | 0.095 |  |  |  | 0.83 |  | 367 |  | 280 |  | single conductor - 600v
Rutgers | 350 |  | 0.095 |  |  |  | 0.88 |  | 420 |  | 305 |  | single conductor - 600v
Dartmouth | 400 |  | 0.095 |  |  |  | 0.92 |  | 476 |  | 330 |  | single conductor - 600v
Emory | 500 |  | 0.095 |  |  |  | 1.01 |  | 577 |  | 370 |  | single conductor - 600v
Duke | 600 |  | 0.110 |  |  |  | 1.12 |  | 697 |  | 410 |  | single conductor - 600v
Furman | 700 |  | 0.110 |  |  |  | 1.20 |  | 804 |  | 440 |  | single conductor - 600v
Sewanee | 750 |  | 0.110 |  |  |  | 1.23 |  | 853 |  | 470 |  | single conductor - 600v
Fordham | 1000 |  | 0.110 |  |  |  | 1.38 |  | 1108 |  | 545 |  | single conductor - 600v
Bard | 8 | 7 | 8 | 7 | 6/1 |  | 0.26 | 0.52 | 69 |  | 55 |  | Duplex Conductor 600 Volt
Claflin | 6 | 7 | 6 | 7 | 6/1 |  | 0.30 | 0.60 | 95 |  | 70 |  | Duplex Conductor 600 Volt
Delgado | 4 | 7 | 4 | 7 | 6/1 |  | 0.35 | 0.69 | 135 |  | 90 |  | Duplex Conductor 600 Volt
Everett | 2 | 7 | 2 | 7 | 6/1 |  | 0.40 | 0.80 | 189 |  | 120 |  | Duplex Conductor 600 Volt
Vassar | 4 | 7 | 0.060 | 4 | 7 |  | 0.30 | 0.64 | 143 |  | 70 |  | Triplex Conductor 600 Volt
Stephens | 2 | 7 | 0.060 | 4 | 7 |  | 0.35 | 0.75 | 202 |  | 90 |  | Triplex Conductor 600 Volt
Ramapo | 2 | 7 | 0.060 | 2 | 7 |  | 0.40 | 0.87 | 262 |  | 120 |  | Triplex Conductor 600 Volt
Brenau | 1/0 | 19 | 0.080 | 2 | 7 |  | 0.40 | 0.87 | 292 |  | 120 |  | Triplex Conductor 600 Volt
Bergen | 1/0 | 19 | 0.080 | 1/0 | 19 |  | 0.51 | 1.11 | 406 |  | 160 |  | Triplex Conductor 600 Volt
Converse | 2/0 | 19 | 0.080 | 1 | 19 |  | 0.51 | 1.11 | 463 |  | 160 |  | Triplex Conductor 600 Volt
Hunter | 2/0 | 19 | 0.080 | 2/0 | 19 |  | 0.56 | 1.20 | 501 |  | 180 |  | Triplex Conductor 600 Volt
Hollins | 3/0 | 19 | 0.080 | 1/0 | 19 |  | 0.56 | 1.20 | 559 |  | 180 |  | Triplex Conductor 600 Volt
Rockland | 3/0 | 19 | 0.080 | 3/0 | 19 |  | 0.60 | 1.30 | 606 |  | 205 |  | Triplex Conductor 600 Volt
Sweetbriar | 4/0 | 19 | 0.080 | 2/0 | 19 |  | 0.60 | 1.30 | 677 |  | 205 |  | Triplex Conductor 600 Volt
Monmouth | 4/0 | 19 | 0.080 | 4/0 | 19 |  | 0.66 | 1.42 | 737 |  | 240 |  | Triplex Conductor 600 Volt
Pratt | 250 | 37 | 0.095 | 3/0 | 19 |  | 0.66 | 1.42 | 826 |  | 240 |  | Triplex Conductor 600 Volt
Wesleyan | 350 | 37 | 0.095 | 4/0 | 19 |  | 0.75 | 1.62 | 888 |  | 265 |  | Triplex Conductor 600 Volt
Holyoke | 500 | 37 | 0.095 | 300 | 37 |  | 0.85 | 1.84 | 1157 |  | 320 |  | Triplex Conductor 600 Volt
Rider | 500 | 37 | 0.095 | 350 | 37 |  | 0.98 | 2.12 | 1591 |  | 395 |  | Triplex Conductor 600 Volt
Fairfield | 750 | 61 | 0.110 | 500 | 37 |  | 0.98 | 2.12 | 1646 |  | 395 |  | Triplex Conductor 600 Volt
Tulsa | 4 | 7 | 0.060 | 4 | 7 |  | 0.35 | 0.83 | 269 |  | 85 |  | Quadruplex Conductor 600 Volt
Dyke | 2 | 7 | 0.060 | 4 | 7 |  | 0.40 | 0.97 | 359 |  | 115 |  | Quadruplex Conductor 600 Volt
Wittenberg | 2 | 7 | 0.060 | 2 | 7 |  | 0.40 | 0.97 | 389 |  | 115 |  | Quadruplex Conductor 600 Volt
Notre_Dame | 1/0 | 19 | 0.080 | 2 | 7 |  | 0.51 | 1.24 | 560 |  | 150 |  | Quadruplex Conductor 600 Volt
Purdue | 1/0 | 19 | 0.080 | 1/0 | 19 |  | 0.51 | 1.24 | 617 |  | 150 |  | Quadruplex Conductor 600 Volt
Syracuse | 2/0 | 19 | 0.080 | 1 | 19 |  | 0.56 | 1.34 | 687 |  | 170 |  | Quadruplex Conductor 600 Volt
Lafayette | 2/0 | 19 | 0.080 | 2/0 | 19 |  | 0.56 | 1.34 | 745 |  | 170 |  | Quadruplex Conductor 600 Volt
Swarthmore | 3/0 | 19 | 0.080 | 1/0 | 19 |  | 0.60 | 1.46 | 832 |  | 195 |  | Quadruplex Conductor 600 Volt
Davidson | 3/0 | 19 | 0.080 | 3/0 | 19 |  | 0.60 | 1.46 | 903 |  | 195 |  | Quadruplex Conductor 600 Volt
Wake_Forest | 4/0 | 19 | 0.080 | 2/0 | 19 |  | 0.66 | 1.59 | 1012 |  | 225 |  | Quadruplex Conductor 600 Volt
Earlham | 4/0 | 19 | 0.080 | 4/0 | 19 |  | 0.66 | 1.59 | 1101 |  | 225 |  | Quadruplex Conductor 600 Volt
Rust | 250 | 37 | 0.095 | 3/0 | 19 |  | 0.75 | 1.81 | 1215 |  | 250 |  | Quadruplex Conductor 600 Volt
Slippery_Rock | 350 | 37 | 0.095 | 4/0 | 19 |  | 0.85 | 2.05 | 1598 |  | 305 |  | Quadruplex Conductor 600 Volt
Niagara | 350 | 37 | 0.095 | 350 | 37 |  | 0.85 | 2.08 | 1695 |  | 305 |  | Quadruplex Conductor 600 Volt
Wofford | 500 | 37 | 0.095 | 350 | 37 |  | 0.98 | 2.35 | 2174 |  | 370 |  | Quadruplex Conductor 600 Volt
Windham | 750 | 61 | 0.110 | 500 | 37 |  | 1.19 | 2.78 | 3305 |  | 460 |  | Quadruplex Conductor 600 Volt

## MV cables
Material | Voltage level | Number of phases | Neutral type | Conductor | Insulation Thickness (mils) | Concentric Neutral | Conductor Diameter (in) | Insulation Diameter (in) | Insulation Shield Diameter (in) | Jacket Diameter (in) | Cable Weight (lbs/kft) | Minimum Bending Radius (in) | Ampacity (Amps) - duct | +/- Sequence Impedance Resistance (µΩ/ft) - duct | +/- Sequence Impedance Reactance (µΩ/ft) - duct | Zero Sequence Impedance Resistance (µΩ/ft) - duct | Zero Sequence Impedance Reactance (µΩ/ft) - duct | Ampacity (Amps) - buried | +/- Sequence Impedance Resistance (µΩ/ft) - buried | +/- Sequence Impedance Reactance (µΩ/ft) - buried | Zero Sequence Impedance Resistance (µΩ/ft) - buried | Zero Sequence Impedance Reactance (µΩ/ft) - buried
100% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 2_SOLID_AL | 175 | 10-#14 | 0.258 | 0.65 | 0.72 | 0.96 | 456 | 8 | 123 | 663 | 29 | 663 | 30 | 169 | 663 | 29 | 663 | 30
100% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 2_AWG_AL | 175 | 10-#14 | 0.284 | 0.68 | 0.75 | 0.99 | 475 | 8 | 124 | 669 | 30 | 669 | 31 | 170 | 669 | 30 | 669 | 31
100% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 1_SOLID_AL | 175 | 13-#14 | 0.289 | 0.69 | 0.75 | 0.99 | 521 | 8 | 141 | 518 | 28 | 518 | 29 | 193 | 518 | 28 | 518 | 29
100% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 1_AWG_AL | 175 | 13-#14 | 0.324 | 0.72 | 0.79 | 1.03 | 545 | 9 | 143 | 523 | 27 | 523 | 28 | 194 | 523 | 27 | 523 | 28
100% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 1/0_SOLID_AL | 175 | 16-#14 | 0.325 | 0.72 | 0.79 | 1.03 | 593 | 9 | 160 | 415 | 27 | 415 | 27 | 219 | 415 | 27 | 415 | 27
100% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 1/0_AWG_AL | 175 | 16-#14 | 0.364 | 0.76 | 0.83 | 1.07 | 621 | 9 | 162 | 420 | 26 | 420 | 26 | 220 | 420 | 26 | 420 | 26
100% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 2/0_AWG_AL | 175 | 13-#12 | 0.408 | 0.80 | 0.87 | 1.14 | 748 | 10 | 186 | 328 | 25 | 328 | 25 | 251 | 328 | 25 | 328 | 25
100% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 3/0_AWG_AL | 175 | 16-#12 | 0.458 | 0.85 | 0.92 | 1.19 | 864 | 10 | 212 | 263 | 24 | 263 | 24 | 284 | 263 | 24 | 263 | 24
100% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 4/0_AWG_AL | 175 | 13-#10 | 0.515 | 0.91 | 0.98 | 1.29 | 1055 | 11 | 243 | 207 | 23 | 207 | 23 | 323 | 207 | 23 | 207 | 23
100% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 250_MCM_AL | 175 | 16-#10 | 0.561 | 0.97 | 1.03 | 1.35 | 1228 | 11 | 270 | 171 | 22 | 171 | 22 | 358 | 171 | 22 | 171 | 22
100% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 350_MCM_AL | 175 | 16-#9 | 0.664 | 1.07 | 1.16 | 1.49 | 1556 | 12 | 321 | 130 | 21 | 130 | 20 | 420 | 130 | 21 | 130 | 20
100% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 2_SOLID_AL | 175 | 6-#14 | 0.258 | 0.65 | 0.72 | 0.96 | 409 | 8 | 126 | 329 | 51 | 872 | 30 | 175 | 338 | 103 | 857 | 30
100% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 2_AWG_AL | 175 | 6-#14 | 0.284 | 0.68 | 0.75 | 0.99 | 429 | 8 | 126 | 335 | 51 | 879 | 31 | 175 | 344 | 102 | 865 | 31
100% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 1_SOLID_AL | 175 | 6-#14 | 0.289 | 0.69 | 0.75 | 0.99 | 440 | 8 | 143 | 261 | 49 | 805 | 29 | 199 | 270 | 100 | 791 | 29
100% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 1_AWG_AL | 175 | 6-#14 | 0.324 | 0.72 | 0.79 | 1.03 | 463 | 9 | 144 | 266 | 48 | 811 | 28 | 199 | 275 | 98 | 798 | 28
100% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 1/0_SOLID_AL | 175 | 6-#14 | 0.325 | 0.72 | 0.79 | 1.03 | 476 | 9 | 163 | 207 | 47 | 752 | 27 | 225 | 216 | 98 | 739 | 27
100% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 1/0_AWG_AL | 175 | 6-#14 | 0.364 | 0.76 | 0.83 | 1.07 | 504 | 9 | 163 | 212 | 46 | 758 | 26 | 225 | 221 | 96 | 745 | 26
100% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 2/0_AWG_AL | 175 | 7-#14 | 0.408 | 0.80 | 0.87 | 1.11 | 564 | 9 | 186 | 168 | 44 | 637 | 25 | 255 | 178 | 93 | 627 | 25
100% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 3/0_AWG_AL | 175 | 9-#14 | 0.458 | 0.85 | 0.92 | 1.16 | 646 | 10 | 212 | 133 | 43 | 498 | 24 | 286 | 145 | 89 | 491 | 24
100% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 4/0_AWG_AL | 175 | 11-#14 | 0.515 | 0.91 | 0.98 | 1.22 | 740 | 10 | 241 | 106 | 41 | 405 | 23 | 320 | 120 | 86 | 400 | 23
100% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 250_MCM_AL | 175 | 13-#14 | 0.561 | 0.97 | 1.03 | 1.27 | 836 | 11 | 265 | 91 | 40 | 343 | 21 | 345 | 106 | 82 | 339 | 21
100% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 350_MCM_AL | 175 | 18-#14 | 0.664 | 1.07 | 1.16 | 1.39 | 1068 | 12 | 319 | 66 | 38 | 247 | 19 | 398 | 84 | 76 | 245 | 19
100% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 500_MCM_AL | 175 | 16-#12 | 0.794 | 1.20 | 1.29 | 1.56 | 1407 | 13 | 385 | 48 | 37 | 174 | 18 | 451 | 68 | 67 | 173 | 18
100% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 750_MCM_AL | 175 | 24-#12 | 0.974 | 1.39 | 1.47 | 1.81 | 1985 | 15 | 468 | 35 | 35 | 117 | 16 | 507 | 57 | 55 | 116 | 16
100% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 1000_MCM_AL | 175 | 20-#10 | 1.124 | 1.54 | 1.65 | 2.03 | 2568 | 17 | 529 | 28 | 33 | 89 | 16 | 549 | 49 | 47 | 88 | 16
133% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 2_SOLID_AL | 220 | 10-#14 | 0.258 | 0.74 | 0.81 | 1.05 | 514 | 9 | 123 | 663 | 29 | 663 | 30 | 169 | 663 | 29 | 663 | 30
133% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 2_AWG_AL | 220 | 10-#14 | 0.284 | 0.77 | 0.84 | 1.08 | 535 | 9 | 124 | 669 | 30 | 669 | 31 | 170 | 669 | 30 | 669 | 31
133% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 1_SOLID_AL | 220 | 13-#14 | 0.289 | 0.78 | 0.84 | 1.08 | 581 | 9 | 141 | 518 | 28 | 518 | 29 | 193 | 518 | 28 | 518 | 29
133% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 1_AWG_AL | 220 | 13-#14 | 0.324 | 0.81 | 0.88 | 1.12 | 607 | 9 | 143 | 523 | 27 | 523 | 28 | 194 | 523 | 27 | 523 | 28
133% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 1/0_SOLID_AL | 220 | 16-#14 | 0.325 | 0.81 | 0.88 | 1.12 | 655 | 9 | 160 | 415 | 27 | 415 | 27 | 219 | 415 | 27 | 415 | 27
133% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 1/0_AWG_AL | 220 | 16-#14 | 0.364 | 0.85 | 0.92 | 1.16 | 685 | 10 | 162 | 420 | 26 | 420 | 26 | 220 | 420 | 26 | 420 | 26
133% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 2/0_AWG_AL | 220 | 13-#12 | 0.408 | 0.89 | 0.96 | 1.23 | 817 | 10 | 186 | 328 | 25 | 328 | 25 | 251 | 328 | 25 | 328 | 25
133% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 3/0_AWG_AL | 220 | 16-#12 | 0.458 | 0.94 | 1.01 | 1.28 | 935 | 11 | 212 | 263 | 24 | 263 | 24 | 284 | 263 | 24 | 263 | 24
133% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 4/0_AWG_AL | 220 | 13-#10 | 0.515 | 1.00 | 1.07 | 1.38 | 1132 | 12 | 243 | 207 | 23 | 207 | 23 | 323 | 207 | 23 | 207 | 23
133% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 250_MCM_AL | 220 | 16-#10 | 0.561 | 1.06 | 1.14 | 1.46 | 1330 | 12 | 270 | 171 | 22 | 171 | 22 | 358 | 171 | 22 | 171 | 22
133% ALUMINUM | 15KV | SINGLE PHASE | FULL NEUTRAL | 350_MCM_AL | 220 | 16-#9 | 0.664 | 1.16 | 1.25 | 1.58 | 1645 | 13 | 321 | 130 | 21 | 130 | 20 | 420 | 130 | 21 | 130 | 20
133% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 2_SOLID_AL | 220 | 6-#14 | 0.258 | 0.74 | 0.81 | 1.05 | 467 | 9 | 126 | 329 | 51 | 872 | 30 | 175 | 338 | 103 | 857 | 30
133% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 2_AWG_AL | 220 | 6-#14 | 0.284 | 0.77 | 0.84 | 1.08 | 488 | 9 | 126 | 335 | 51 | 879 | 31 | 175 | 344 | 102 | 865 | 31
133% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 1_SOLID_AL | 220 | 6-#14 | 0.289 | 0.78 | 0.84 | 1.08 | 499 | 9 | 143 | 261 | 49 | 805 | 29 | 199 | 270 | 100 | 791 | 29
133% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 1_AWG_AL | 220 | 6-#14 | 0.324 | 0.81 | 0.88 | 1.12 | 525 | 9 | 144 | 266 | 48 | 811 | 28 | 199 | 275 | 98 | 798 | 28
133% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 1/0_SOLID_AL | 220 | 6-#14 | 0.325 | 0.81 | 0.88 | 1.12 | 538 | 9 | 163 | 207 | 47 | 752 | 27 | 225 | 216 | 98 | 739 | 27
133% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 1/0_AWG_AL | 220 | 6-#14 | 0.364 | 0.85 | 0.92 | 1.16 | 568 | 10 | 163 | 212 | 46 | 758 | 26 | 225 | 221 | 96 | 745 | 26
133% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 2/0_AWG_AL | 220 | 7-#14 | 0.408 | 0.89 | 0.96 | 1.20 | 630 | 10 | 186 | 168 | 44 | 637 | 25 | 255 | 178 | 93 | 627 | 25
133% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 3/0_AWG_AL | 220 | 9-#14 | 0.458 | 0.94 | 1.01 | 1.25 | 715 | 11 | 212 | 133 | 43 | 498 | 24 | 286 | 145 | 89 | 491 | 24
133% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 4/0_AWG_AL | 220 | 11-#14 | 0.515 | 1.00 | 1.07 | 1.31 | 813 | 11 | 241 | 106 | 41 | 405 | 23 | 320 | 120 | 86 | 400 | 23
133% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 250_MCM_AL | 220 | 13-#14 | 0.561 | 1.06 | 1.14 | 1.38 | 932 | 12 | 265 | 91 | 40 | 343 | 21 | 345 | 106 | 82 | 339 | 21
133% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 350_MCM_AL | 220 | 18-#14 | 0.664 | 1.16 | 1.25 | 1.48 | 1150 | 12 | 319 | 66 | 38 | 247 | 19 | 398 | 84 | 76 | 245 | 19
133% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 500_MCM_AL | 220 | 16-#12 | 0.794 | 1.29 | 1.38 | 1.71 | 1563 | 14 | 385 | 48 | 37 | 174 | 18 | 451 | 68 | 67 | 173 | 18
133% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 750_MCM_AL | 220 | 24-#12 | 0.974 | 1.48 | 1.56 | 1.90 | 2091 | 16 | 468 | 35 | 35 | 117 | 16 | 507 | 57 | 55 | 116 | 16
133% ALUMINUM | 15KV | THREE PHASE | ONE-THIRD NEUTRAL | 1000_MCM_AL | 220 | 20-#10 | 1.124 | 1.63 | 1.74 | 2.12 | 2687 | 17 | 529 | 28 | 33 | 89 | 16 | 549 | 49 | 47 | 88 | 16
100% ALUMINUM | 25KV | SINGLE PHASE | FULL NEUTRAL | 1_SOLID_AL | 260 | 13-#14 | 0.289 | 0.86 | 0.92 | 1.16 | 638 | 10 | 145 | 518 | 33 | 518 | 33 | 192 | 518 | 33 | 518 | 33
100% ALUMINUM | 25KV | SINGLE PHASE | FULL NEUTRAL | 1_AWG_AL | 260 | 13-#14 | 0.324 | 0.89 | 0.96 | 1.20 | 666 | 10 | 146 | 523 | 31 | 523 | 32 | 194 | 523 | 31 | 523 | 32
100% ALUMINUM | 25KV | SINGLE PHASE | FULL NEUTRAL | 1/0_SOLID_AL | 260 | 16-#14 | 0.325 | 0.89 | 0.96 | 1.20 | 714 | 10 | 165 | 415 | 31 | 415 | 31 | 218 | 415 | 31 | 415 | 31
100% ALUMINUM | 25KV | SINGLE PHASE | FULL NEUTRAL | 1/0_AWG_AL | 260 | 16-#14 | 0.364 | 0.93 | 1.00 | 1.24 | 746 | 10 | 166 | 420 | 30 | 420 | 30 | 219 | 420 | 30 | 420 | 30
100% ALUMINUM | 25KV | SINGLE PHASE | FULL NEUTRAL | 2/0_AWG_AL | 260 | 13-#12 | 0.408 | 0.97 | 1.04 | 1.31 | 882 | 11 | 190 | 328 | 29 | 328 | 29 | 250 | 328 | 29 | 328 | 29
100% ALUMINUM | 25KV | SINGLE PHASE | FULL NEUTRAL | 3/0_AWG_AL | 260 | 16-#12 | 0.458 | 1.02 | 1.11 | 1.38 | 1023 | 12 | 217 | 263 | 28 | 263 | 28 | 283 | 263 | 28 | 263 | 28
100% ALUMINUM | 25KV | SINGLE PHASE | FULL NEUTRAL | 4/0_AWG_AL | 260 | 13-#10 | 0.515 | 1.08 | 1.17 | 1.48 | 1227 | 12 | 248 | 207 | 26 | 207 | 27 | 322 | 207 | 26 | 207 | 27
100% ALUMINUM | 25KV | SINGLE PHASE | FULL NEUTRAL | 250_MCM_AL | 260 | 16-#10 | 0.561 | 1.14 | 1.22 | 1.54 | 1406 | 13 | 276 | 171 | 25 | 171 | 25 | 356 | 171 | 25 | 171 | 25
100% ALUMINUM | 25KV | SINGLE PHASE | FULL NEUTRAL | 350_MCM_AL | 260 | 16-#9 | 0.664 | 1.24 | 1.33 | 1.72 | 1792 | 14 | 326 | 130 | 23 | 130 | 23 | 416 | 130 | 23 | 130 | 23
100% ALUMINUM | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 1_SOLID_AL | 260 | 6-#14 | 0.289 | 0.86 | 0.92 | 1.16 | 556 | 10 | 146 | 261 | 53 | 801 | 33 | 196 | 269 | 101 | 786 | 33
100% ALUMINUM | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 1_AWG_AL | 260 | 6-#14 | 0.324 | 0.89 | 0.96 | 1.20 | 584 | 10 | 146 | 266 | 52 | 807 | 32 | 196 | 274 | 99 | 792 | 32
100% ALUMINUM | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 1/0_SOLID_AL | 260 | 6-#14 | 0.325 | 0.89 | 0.96 | 1.20 | 597 | 10 | 166 | 207 | 51 | 748 | 31 | 222 | 215 | 98 | 734 | 31
100% ALUMINUM | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 1/0_AWG_AL | 260 | 6-#14 | 0.364 | 0.93 | 1.00 | 1.24 | 629 | 10 | 166 | 212 | 50 | 754 | 30 | 222 | 220 | 96 | 740 | 30
100% ALUMINUM | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 2/0_AWG_AL | 260 | 7-#14 | 0.408 | 0.97 | 1.04 | 1.28 | 694 | 11 | 189 | 168 | 48 | 634 | 29 | 251 | 177 | 93 | 622 | 29
100% ALUMINUM | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 3/0_AWG_AL | 260 | 9-#14 | 0.458 | 1.02 | 1.11 | 1.35 | 801 | 11 | 216 | 133 | 46 | 495 | 27 | 283 | 144 | 90 | 487 | 27
100% ALUMINUM | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 4/0_AWG_AL | 260 | 11-#14 | 0.515 | 1.08 | 1.17 | 1.41 | 902 | 12 | 245 | 106 | 45 | 403 | 26 | 317 | 119 | 86 | 397 | 26
100% ALUMINUM | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 250_MCM_AL | 260 | 13-#14 | 0.561 | 1.14 | 1.22 | 1.46 | 1004 | 12 | 269 | 90 | 43 | 341 | 25 | 343 | 104 | 83 | 337 | 25
100% ALUMINUM | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 350_MCM_AL | 260 | 18-#14 | 0.664 | 1.24 | 1.33 | 1.56 | 1228 | 13 | 322 | 66 | 41 | 246 | 23 | 397 | 82 | 76 | 244 | 23
100% ALUMINUM | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 500_MCM_AL | 260 | 16-#12 | 0.794 | 1.37 | 1.46 | 1.79 | 1652 | 15 | 389 | 48 | 40 | 173 | 21 | 451 | 67 | 68 | 172 | 21
100% ALUMINUM | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 750_MCM_AL | 260 | 24-#12 | 0.974 | 1.56 | 1.67 | 2.01 | 2234 | 17 | 473 | 34 | 37 | 116 | 19 | 513 | 55 | 57 | 116 | 19
100% ALUMINUM | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 1000_MCM_AL | 260 | 20-#10 | 1.124 | 1.71 | 1.82 | 2.20 | 2797 | 18 | 533 | 28 | 35 | 88 | 18 | 555 | 48 | 49 | 88 | 18
133% ALUMINUM | 25KV | SINGLE PHASE | FULL NEUTRAL | 1_SOLID_AL | 320 | 13-#14 | 0.289 | 0.98 | 1.05 | 1.29 | 735 | 11 | 145 | 518 | 33 | 518 | 33 | 192 | 518 | 33 | 518 | 33
133% ALUMINUM | 25KV | SINGLE PHASE | FULL NEUTRAL | 1_AWG_AL | 320 | 13-#14 | 0.324 | 1.01 | 1.08 | 1.32 | 765 | 11 | 146 | 523 | 31 | 523 | 32 | 194 | 523 | 31 | 523 | 32
133% ALUMINUM | 25KV | SINGLE PHASE | FULL NEUTRAL | 1/0_SOLID_AL | 320 | 16-#14 | 0.325 | 1.02 | 1.08 | 1.32 | 813 | 11 | 165 | 415 | 31 | 415 | 31 | 218 | 415 | 31 | 415 | 31
133% ALUMINUM | 25KV | SINGLE PHASE | FULL NEUTRAL | 1/0_AWG_AL | 320 | 16-#14 | 0.364 | 1.05 | 1.14 | 1.38 | 869 | 12 | 166 | 420 | 30 | 420 | 30 | 219 | 420 | 30 | 420 | 30
133% ALUMINUM | 25KV | SINGLE PHASE | FULL NEUTRAL | 2/0_AWG_AL | 320 | 13-#12 | 0.408 | 1.10 | 1.19 | 1.46 | 1012 | 12 | 190 | 328 | 29 | 328 | 29 | 250 | 328 | 29 | 328 | 29
133% ALUMINUM | 25KV | SINGLE PHASE | FULL NEUTRAL | 3/0_AWG_AL | 320 | 16-#12 | 0.458 | 1.15 | 1.24 | 1.51 | 1137 | 13 | 217 | 263 | 28 | 263 | 28 | 283 | 263 | 28 | 263 | 28
133% ALUMINUM | 25KV | SINGLE PHASE | FULL NEUTRAL | 4/0_AWG_AL | 320 | 13-#10 | 0.515 | 1.21 | 1.29 | 1.61 | 1349 | 13 | 248 | 207 | 26 | 207 | 27 | 322 | 207 | 26 | 207 | 27
133% ALUMINUM | 25KV | SINGLE PHASE | FULL NEUTRAL | 250_MCM_AL | 320 | 16-#10 | 0.561 | 1.26 | 1.35 | 1.72 | 1597 | 14 | 276 | 171 | 25 | 171 | 25 | 356 | 171 | 25 | 171 | 25
133% ALUMINUM | 25KV | SINGLE PHASE | FULL NEUTRAL | 350_MCM_AL | 320 | 16-#9 | 0.664 | 1.36 | 1.45 | 1.85 | 1934 | 15 | 326 | 130 | 23 | 130 | 23 | 416 | 130 | 23 | 130 | 23
133% ALUMINUM T | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 1_SOLID_AL | 320 | 6-#14 | 0.289 | 0.98 | 1.05 | 1.29 | 653 | 11 | 146 | 261 | 53 | 801 | 33 | 196 | 269 | 101 | 786 | 33
133% ALUMINUM T | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 1_AWG_AL | 320 | 6-#14 | 0.324 | 1.01 | 1.08 | 1.32 | 683 | 11 | 146 | 266 | 52 | 807 | 32 | 196 | 274 | 99 | 792 | 32
133% ALUMINUM T | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 1/0_SOLID_AL | 320 | 6-#14 | 0.325 | 1.02 | 1.08 | 1.32 | 696 | 11 | 166 | 207 | 51 | 748 | 31 | 222 | 215 | 98 | 734 | 31
133% ALUMINUM T | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 1/0_AWG_AL | 320 | 6-#14 | 0.364 | 1.05 | 1.14 | 1.38 | 752 | 12 | 166 | 212 | 50 | 754 | 30 | 222 | 220 | 96 | 740 | 30
133% ALUMINUM T | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 2/0_AWG_AL | 320 | 7-#14 | 0.408 | 1.10 | 1.19 | 1.42 | 821 | 12 | 189 | 168 | 48 | 634 | 29 | 251 | 177 | 93 | 622 | 29
133% ALUMINUM T | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 3/0_AWG_AL | 320 | 9-#14 | 0.458 | 1.15 | 1.24 | 1.47 | 912 | 12 | 216 | 133 | 46 | 495 | 27 | 283 | 144 | 90 | 487 | 27
133% ALUMINUM T | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 4/0_AWG_AL | 320 | 11-#14 | 0.515 | 1.21 | 1.29 | 1.53 | 1018 | 13 | 245 | 106 | 45 | 403 | 26 | 317 | 119 | 86 | 397 | 26
133% ALUMINUM T | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 250_MCM_AL | 320 | 13-#14 | 0.561 | 1.26 | 1.35 | 1.59 | 1125 | 13 | 269 | 90 | 43 | 341 | 25 | 343 | 104 | 83 | 337 | 25
133% ALUMINUM T | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 350_MCM_AL | 320 | 18-#14 | 0.664 | 1.36 | 1.45 | 1.75 | 1422 | 14 | 322 | 66 | 41 | 246 | 23 | 397 | 82 | 76 | 244 | 23
133% ALUMINUM T | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 500_MCM_AL | 320 | 16-#12 | 0.794 | 1.49 | 1.58 | 1.91 | 1797 | 16 | 389 | 48 | 40 | 173 | 21 | 451 | 67 | 68 | 172 | 21
133% ALUMINUM T | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 750_MCM_AL | 320 | 24-#12 | 0.974 | 1.68 | 1.80 | 2.13 | 2398 | 18 | 473 | 34 | 37 | 116 | 19 | 513 | 55 | 57 | 116 | 19
133% ALUMINUM T | 25KV | THREE PHASE | ONE-THIRD NEUTRAL | 1000_MCM_AL | 320 | 20-#10 | 1.124 | 1.83 | 1.95 | 2.32 | 2975 | 19 | 533 | 28 | 35 | 88 | 18 | 555 | 48 | 49 | 88 | 18
100% ALUMINUM | 35KV | SINGLE PHASE | FULL NEUTRAL | 1/0_SOLID_AL | 345 | 16-#14 | 0.325 | 1.07 | 1.15 | 1.39 | 877 | 12 | 168 | 415 | 35 | 415 | 35 | 217 | 415 | 35 | 415 | 35
100% ALUMINUM | 35KV | SINGLE PHASE | FULL NEUTRAL | 1/0_AWG_AL | 345 | 16-#14 | 0.364 | 1.10 | 1.19 | 1.43 | 914 | 12 | 169 | 420 | 34 | 420 | 34 | 218 | 420 | 34 | 420 | 34
100% ALUMINUM | 35KV | SINGLE PHASE | FULL NEUTRAL | 2/0_AWG_AL | 345 | 13-#12 | 0.408 | 1.15 | 1.24 | 1.51 | 1059 | 13 | 194 | 328 | 32 | 328 | 33 | 249 | 328 | 32 | 328 | 33
100% ALUMINUM | 35KV | SINGLE PHASE | FULL NEUTRAL | 3/0_AWG_AL | 345 | 16-#12 | 0.458 | 1.20 | 1.29 | 1.56 | 1186 | 13 | 220 | 263 | 31 | 263 | 31 | 283 | 263 | 31 | 263 | 31
100% ALUMINUM | 35KV | SINGLE PHASE | FULL NEUTRAL | 4/0_AWG_AL | 345 | 13-#10 | 0.515 | 1.26 | 1.34 | 1.72 | 1465 | 14 | 252 | 207 | 30 | 207 | 30 | 321 | 207 | 30 | 207 | 30
100% ALUMINUM | 35KV | SINGLE PHASE | FULL NEUTRAL | 250_MCM_AL | 345 | 16-#10 | 0.561 | 1.31 | 1.40 | 1.77 | 1653 | 15 | 280 | 171 | 28 | 171 | 28 | 353 | 171 | 28 | 171 | 28
100% ALUMINUM | 35KV | SINGLE PHASE | FULL NEUTRAL | 350_MCM_AL | 345 | 16-#9 | 0.664 | 1.41 | 1.50 | 1.90 | 1993 | 16 | 331 | 130 | 26 | 130 | 26 | 416 | 130 | 26 | 130 | 26
100% ALUMINUM | 35KV | THREE PHASE | ONE-THIRD NEUTRAL | 1/0_SOLID_AL | 345 | 6-#14 | 0.325 | 1.07 | 1.15 | 1.39 | 760 | 12 | 168 | 207 | 54 | 745 | 35 | 219 | 214 | 98 | 729 | 35
100% ALUMINUM | 35KV | THREE PHASE | ONE-THIRD NEUTRAL | 1/0_AWG_AL | 345 | 6-#14 | 0.364 | 1.10 | 1.19 | 1.43 | 797 | 12 | 168 | 212 | 53 | 751 | 34 | 219 | 219 | 96 | 736 | 34
100% ALUMINUM | 35KV | THREE PHASE | ONE-THIRD NEUTRAL | 2/0_AWG_AL | 345 | 7-#14 | 0.408 | 1.15 | 1.24 | 1.47 | 867 | 12 | 191 | 168 | 51 | 631 | 32 | 248 | 176 | 93 | 618 | 32
100% ALUMINUM | 35KV | THREE PHASE | ONE-THIRD NEUTRAL | 3/0_AWG_AL | 345 | 9-#14 | 0.458 | 1.20 | 1.29 | 1.52 | 960 | 13 | 218 | 133 | 49 | 493 | 31 | 280 | 143 | 90 | 485 | 31
100% ALUMINUM | 35KV | THREE PHASE | ONE-THIRD NEUTRAL | 4/0_AWG_AL | 345 | 11-#14 | 0.515 | 1.26 | 1.34 | 1.58 | 1068 | 13 | 247 | 106 | 47 | 401 | 29 | 314 | 117 | 86 | 395 | 29
100% ALUMINUM | 35KV | THREE PHASE | ONE-THIRD NEUTRAL | 250_MCM_AL | 345 | 13-#14 | 0.561 | 1.31 | 1.40 | 1.70 | 1239 | 14 | 271 | 90 | 47 | 340 | 28 | 339 | 103 | 83 | 335 | 28
100% ALUMINUM | 35KV | THREE PHASE | ONE-THIRD NEUTRAL | 350_MCM_AL | 345 | 18-#14 | 0.664 | 1.41 | 1.50 | 1.80 | 1478 | 15 | 325 | 66 | 44 | 245 | 25 | 394 | 81 | 77 | 243 | 25
100% ALUMINUM | 35KV | THREE PHASE | ONE-THIRD NEUTRAL | 500_MCM_AL | 345 | 16-#12 | 0.794 | 1.54 | 1.66 | 1.99 | 1904 | 16 | 392 | 48 | 42 | 173 | 24 | 452 | 65 | 69 | 171 | 24
100% ALUMINUM | 35KV | THREE PHASE | ONE-THIRD NEUTRAL | 750_MCM_AL | 345 | 24-#12 | 0.974 | 1.73 | 1.85 | 2.18 | 2466 | 18 | 476 | 34 | 39 | 116 | 21 | 517 | 54 | 59 | 115 | 21
100% ALUMINUM | 35KV | THREE PHASE | ONE-THIRD NEUTRAL | 1000_MCM_AL | 345 | 20-#10 | 1.124 | 1.88 | 2.00 | 2.37 | 3050 | 19 | 536 | 28 | 37 | 88 | 20 | 560 | 47 | 51 | 88 | 20
133% ALUMINUM | 35KV | SINGLE PHASE | FULL NEUTRAL | 1/0_SOLID_AL | 420 | 16-#14 | 0.325 | 1.22 | 1.31 | 1.55 | 1021 | 13 | 168 | 415 | 35 | 415 | 35 | 217 | 415 | 35 | 415 | 35
133% ALUMINUM | 35KV | SINGLE PHASE | FULL NEUTRAL | 1/0_AWG_AL | 420 | 16-#14 | 0.364 | 1.26 | 1.35 | 1.58 | 1062 | 13 | 169 | 420 | 34 | 420 | 34 | 218 | 420 | 34 | 420 | 34
133% ALUMINUM | 35KV | SINGLE PHASE | FULL NEUTRAL | 2/0_AWG_AL | 420 | 13-#12 | 0.408 | 1.30 | 1.39 | 1.72 | 1279 | 14 | 194 | 328 | 32 | 328 | 33 | 249 | 328 | 32 | 328 | 33
133% ALUMINUM | 35KV | SINGLE PHASE | FULL NEUTRAL | 3/0_AWG_AL | 420 | 16-#12 | 0.458 | 1.35 | 1.44 | 1.77 | 1412 | 15 | 220 | 263 | 31 | 263 | 31 | 283 | 263 | 31 | 263 | 31
133% ALUMINUM | 35KV | SINGLE PHASE | FULL NEUTRAL | 4/0_AWG_AL | 420 | 13-#10 | 0.515 | 1.41 | 1.50 | 1.87 | 1641 | 15 | 252 | 207 | 30 | 207 | 30 | 321 | 207 | 30 | 207 | 30
133% ALUMINUM | 35KV | SINGLE PHASE | FULL NEUTRAL | 250_MCM_AL | 420 | 16-#10 | 0.561 | 1.46 | 1.55 | 1.93 | 1834 | 16 | 280 | 171 | 28 | 171 | 28 | 353 | 171 | 28 | 171 | 28
133% ALUMINUM | 35KV | SINGLE PHASE | FULL NEUTRAL | 350_MCM_AL | 420 | 16-#9 | 0.664 | 1.57 | 1.68 | 2.08 | 2234 | 17 | 331 | 130 | 26 | 130 | 26 | 416 | 130 | 26 | 130 | 26
133% ALUMINUM | 35KV | THREE PHASE | ONE THIRD NEUTRAL | 1/0_SOLID_AL | 420 | 6-#14 | 0.325 | 1.22 | 1.31 | 1.55 | 904 | 13 | 168 | 207 | 54 | 745 | 35 | 219 | 214 | 98 | 729 | 35
133% ALUMINUM | 35KV | THREE PHASE | ONE THIRD NEUTRAL | 1/0_AWG_AL | 420 | 6-#14 | 0.364 | 1.26 | 1.35 | 1.58 | 945 | 13 | 168 | 212 | 53 | 751 | 34 | 219 | 219 | 96 | 736 | 34
133% ALUMINUM | 35KV | THREE PHASE | ONE THIRD NEUTRAL | 2/0_AWG_AL | 420 | 7-#14 | 0.408 | 1.30 | 1.39 | 1.63 | 1019 | 14 | 191 | 168 | 51 | 631 | 32 | 248 | 176 | 93 | 618 | 32
133% ALUMINUM | 35KV | THREE PHASE | ONE THIRD NEUTRAL | 3/0_AWG_AL | 420 | 9-#14 | 0.458 | 1.35 | 1.44 | 1.74 | 1182 | 14 | 218 | 133 | 49 | 493 | 31 | 280 | 143 | 90 | 485 | 31
133% ALUMINUM | 35KV | THREE PHASE | ONE THIRD NEUTRAL | 4/0_AWG_AL | 420 | 11-#14 | 0.515 | 1.41 | 1.50 | 1.80 | 1297 | 15 | 247 | 106 | 47 | 401 | 29 | 314 | 117 | 86 | 395 | 29
133% ALUMINUM | 35KV | THREE PHASE | ONE THIRD NEUTRAL | 250_MCM_AL | 420 | 13-#14 | 0.561 | 1.46 | 1.55 | 1.85 | 1412 | 15 | 271 | 90 | 47 | 340 | 28 | 339 | 103 | 83 | 335 | 28
133% ALUMINUM | 35KV | THREE PHASE | ONE THIRD NEUTRAL | 350_MCM_AL | 420 | 18-#14 | 0.664 | 1.57 | 1.68 | 1.98 | 1706 | 16 | 325 | 66 | 44 | 245 | 25 | 394 | 81 | 77 | 243 | 25
133% ALUMINUM | 35KV | THREE PHASE | ONE THIRD NEUTRAL | 500_MCM_AL | 420 | 16-#12 | 0.794 | 1.70 | 1.81 | 2.15 | 2107 | 18 | 392 | 48 | 42 | 173 | 24 | 452 | 65 | 69 | 171 | 24
133% ALUMINUM | 35KV | THREE PHASE | ONE THIRD NEUTRAL | 750_MCM_AL | 420 | 24-#12 | 0.974 | 1.88 | 2.00 | 2.33 | 2687 | 19 | 476 | 34 | 39 | 116 | 21 | 517 | 54 | 59 | 115 | 21
133% ALUMINUM | 35KV | THREE PHASE | ONE THIRD NEUTRAL | 1000_MCM_AL | 420 | 20-#10 | 1.124 | 2.03 | 2.15 | 2.53 | 3290 | 21 | 536 | 28 | 37 | 88 | 20 | 560 | 47 | 51 | 88 | 20

## General purpose copper cables
AWG | No. of Conductors | No. of Strands | Insulation Thickness (inches) | Jacket Thickness (inches) | Overall Diameter (inches) | Weight (lbs/kft) | Shielding | Configuration
14 | 2 | 7 | 0.030 | 0.045 | 0.36 | 71
14 | 3 | 7 | 0.030 | 0.045 | 0.38 | 93
14 | 4 | 7 | 0.030 | 0.045 | 0.41 | 116
14 | 5 | 7 | 0.030 | 0.045 | 0.45 | 140
14 | 7 | 7 | 0.030 | 0.045 | 0.49 | 187
14 | 9 | 7 | 0.030 | 0.060 | 0.60 | 255
14 | 12 | 7 | 0.030 | 0.060 | 0.68 | 328
14 | 19 | 7 | 0.030 | 0.080 | 0.79 | 487
14 | 25 | 7 | 0.030 | 0.080 | 0.93 | 663
14 | 30 | 7 | 0.030 | 0.080 | 1.00 | 780
14 | 37 | 7 | 0.030 | 0.080 | 1.10 | 940
12 | 2 | 7 | 0.030 | 0.045 | 0.39 | 100
12 | 3 | 7 | 0.030 | 0.045 | 0.42 | 130
12 | 4 | 7 | 0.030 | 0.045 | 0.45 | 163
12 | 5 | 7 | 0.030 | 0.045 | 0.50 | 194
12 | 7 | 7 | 0.030 | 0.060 | 0.58 | 274
12 | 9 | 7 | 0.030 | 0.060 | 0.67 | 359
12 | 12 | 7 | 0.030 | 0.060 | 0.75 | 445
12 | 15 | 7 | 0.030 | 0.080 | 0.87 | 603
12 | 19 | 7 | 0.030 | 0.080 | 0.92 | 709
12 | 25 | 7 | 0.030 | 0.080 | 1.03 | 907
12 | 30 | 7 | 0.030 | 0.080 | 1.13 | 1074
12 | 37 | 7 | 0.030 | 0.080 | 1.24 | 1288
10 | 2 | 7 | 0.030 | 0.045 | 0.44 | 133
10 | 3 | 7 | 0.030 | 0.045 | 0.47 | 185
10 | 4 | 7 | 0.030 | 0.060 | 0.55 | 252
10 | 5 | 7 | 0.030 | 0.060 | 0.60 | 299
10 | 7 | 7 | 0.030 | 0.060 | 0.65 | 395
10 | 9 | 7 | 0.030 | 0.060 | 0.76 | 510
10 | 12 | 7 | 0.030 | 0.080 | 0.89 | 687
10 | 15 | 7 | 0.030 | 0.080 | 0.96 | 735
10 | 19 | 7 | 0.030 | 0.080 | 1.04 | 1032
10 | 25 | 7 | 0.030 | 0.080 | 1.19 | 1170
10 | 37 | 7 | 0.030 | 0.080 | 1.41 | 1680
12 | 2 | 12 | 0.030 | 0.045 | 0.41 | 105
12 | 3 | 12 | 0.030 | 0.045 | 0.43 | 140
12 | 4 | 12 | 0.030 | 0.045 | 0.47 | 170
10 | 2 | 10 | 0.030 | 0.045 | 0.47 | 183
10 | 3 | 10 | 0.030 | 0.060 | 0.54 | 246
10 | 4 | 10 | 0.030 | 0.060 | 0.60 | 302
8 | 2 | 10 | 0.045 | 0.060 | 0.65 | 362
8 | 3 | 10 | 0.045 | 0.060 | 0.66 | 373
8 | 4 | 10 | 0.045 | 0.060 | 0.74 | 415
6 | 2 | 8 | 0.045 | 0.060 | 0.69 | 393
6 | 3 | 8 | 0.045 | 0.060 | 0.76 | 531
6 | 4 | 8 | 0.045 | 0.060 | 0.84 | 650
4 | 2 | 8 | 0.045 | 0.060 | 0.77 | 537
4 | 3 | 8 | 0.045 | 0.080 | 0.93 | 778
4 | 4 | 8 | 0.045 | 0.080 | 1.00 | 909
2 | 3 | 6 | 0.045 | 0.080 | 1.03 | 1155
2 | 4 | 6 | 0.045 | 0.080 | 1.15 | 1429
18 | 3 |  | 0.015/0.010 | 0.045 | 0.294 | 47 | Unshielded | 15/10 PE/PVC - 7 Strand
18 | 4 |  | 0.015/0.010 | 0.045 | 0.319 | 58 | Unshielded | 15/10 PE/PVC - 7 Strand
18 | 7 |  | 0.015/0.010 | 0.045 | 0.378 | 89 | Unshielded | 15/10 PE/PVC - 7 Strand
18 | 12 |  | 0.015/0.010 | 0.045 | 0.490 | 142 | Unshielded | 15/10 PE/PVC - 7 Strand
14 | 4 |  | 0.020/0.010 | 0.045 | 0.411 | 106 | Unshielded | 20/10 PE/PVC - 7 Strand
14 | 7 |  | 0.020/0.010 | 0.045 | 0.492 | 170 | Unshielded | 20/10 PE/PVC - 7 Strand
14 | 12 |  | 0.020/0.010 | 0.060 | 0.678 | 299 | Unshielded | 20/10 PE/PVC - 7 Strand
12 | 2 |  | 0.020/0.010 | 0.045 | 0.393 | 93 | Unshielded | 20/10 PE/PVC - 7 Strand
12 | 3 |  | 0.020/0.010 | 0.045 | 0.415 | 121 | Unshielded | 20/10 PE/PVC - 7 Strand
12 | 4 |  | 0.020/0.010 | 0.045 | 0.454 | 147 | Unshielded | 20/10 PE/PVC - 7 Strand
12 | 7 |  | 0.020/0.010 | 0.060 | 0.591 | 256 | Unshielded | 20/10 PE/PVC - 7 Strand
12 | 8 |  | 0.020/0.010 | 0.060 | 0.622 | 291 | Unshielded | 20/10 PE/PVC - 7 Strand
12 | 9 |  | 0.020/0.010 | 0.060 | 0.690 | 330 | Unshielded | 20/10 PE/PVC - 7 Strand
12 | 12 |  | 0.020/0.010 | 0.060 | 0.749 | 413 | Unshielded | 20/10 PE/PVC - 7 Strand
10 | 2 |  | 0.020/0.010 | 0.045 | 0.439 | 128 | Unshielded | 20/10 PE/PVC - 7 Strand
10 | 3 |  | 0.020/0.010 | 0.045 | 0.465 | 128 | Unshielded | 20/10 PE/PVC - 7 Strand
10 | 4 |  | 0.020/0.010 | 0.045 | 0.513 | 214 | Unshielded | 20/10 PE/PVC - 7 Strand
10 | 5 |  | 0.020/0.010 | 0.060 | 0.609 | 286 | Unshielded | 20/10 PE/PVC - 7 Strand
10 | 7 |  | 0.020/0.010 | 0.060 | 0.642 | 356 | Unshielded | 20/10 PE/PVC - 7 Strand
10 | 8 |  | 0.020/0.010 | 0.060 | 0.696 | 409 | Unshielded | 20/10 PE/PVC - 7 Strand
10 | 9 |  | 0.020/0.010 | 0.060 | 0.749 | 451 | Unshielded | 20/10 PE/PVC - 7 Strand
10 | 12 |  | 0.020/0.010 | 0.080 | 0.884 | 629 | Unshielded | 20/10 PE/PVC - 7 Strand
18 | 2 |  | 0.030/0.015 | 0.045 | 0.390 | 62 | Unshielded | 30/15 PE/PVC - 7 Strand
14 | 6 |  | 0.030/0.015 | 0.060 | 0.635 | 220 | Unshielded | 30/15 PE/PVC - 7 Strand
12 | 2 |  | 0.030/0.015 | 0.045 | 0.470 | 102 | Unshielded | 30/15 PE/PVC - 7 Strand
12 | 4 |  | 0.030/0.015 | 0.060 | 0.580 | 188 | Unshielded | 30/15 PE/PVC - 7 Strand
10 | 4 |  | 0.030/0.015 | 0.060 | 0.640 | 250 | Unshielded | 30/15 PE/PVC - 7 Strand
10 | 8 |  | 0.030/0.015 | 0.080 | 0.900 | 490 | Unshielded | 30/15 PE/PVC - 7 Strand
6 | 4 |  | 0.030/0.015 | 0.060 | 0.800 | 495 | Unshielded | 30/15 PE/PVC - 7 Strand
8 | 2 |  | 0.045/0.015 | 0.060 | 0.645 | 238 | Unshielded | 45/15 PE/PVC - 7 Strand
8 | 3 |  | 0.045/0.015 | 0.060 | 0.684 | 309 | Unshielded | 45/15 PE/PVC - 7 Strand
8 | 12 |  | 0.045/0.015 | 0.080 | 1.249 | 1066 | Unshielded | 45/15 PE/PVC - 7 Strand
6 | 2 |  | 0.045/0.025 | 0.060 | 0.774 | 351 | Unshielded | 45/25 PE/PVC - 7 Strand
6 | 3 |  | 0.045/0.025 | 0.080 | 0.863 | 500 | Unshielded | 45/25 PE/PVC - 7 Strand
4 | 3 |  | 0.045/0.025 | 0.080 | 0.966 | 673 | Unshielded | 45/25 PE/PVC - 7 Strand
18 | 3 |  | 0.015/0.010 | 0.045 | 0.307 | 76 | Shielded | 15/10 PE/PVC - 7 Strand
18 | 4 |  | 0.015/0.010 | 0.045 | 0.332 | 89 | Shielded | 15/10 PE/PVC - 7 Strand
18 | 7 |  | 0.015/0.010 | 0.045 | 0.388 | 116 | Shielded | 15/10 PE/PVC - 7 Strand
18 | 12 |  | 0.015/0.010 | 0.045 | 0.497 | 177 | Shielded | 15/10 PE/PVC - 7 Strand
14 | 7 |  | 0.020/0.010 | 0.045 | 0.499 | 206 | Shielded | 20/10 PE/PVC - 7 Strand
12 | 2 |  | 0.020/0.010 | 0.045 | 0.403 | 128 | Shielded | 20/10 PE/PVC - 7 Strand
10 | 2 |  | 0.020/0.010 | 0.045 | 0.449 | 154 | Shielded | 20/10 PE/PVC - 7 Strand
10 | 3 |  | 0.020/0.010 | 0.045 | 0.475 | 202 | Shielded | 20/10 PE/PVC - 7 Strand
10 | 4 |  | 0.020/0.010 | 0.060 | 0.550 | 267 | Shielded | 20/10 PE/PVC - 7 Strand
10 | 5 |  | 0.020/0.010 | 0.060 | 0.969 | 719 | Shielded | 20/10 PE/PVC - 7 Strand
10 | 8 |  | 0.020/0.010 | 0.060 | 0.706 | 458 | Shielded | 20/10 PE/PVC - 7 Strand
10 | 9 |  | 0.020/0.010 | 0.060 | 0.759 | 505 | Shielded | 20/10 PE/PVC - 7 Strand
10 | 12 |  | 0.020/0.010 | 0.080 | 0.891 | 688 | Shielded | 20/10 PE/PVC - 7 Strand
18 | 2 |  | 0.030/0.015 | 0.045 | 0.400 | 87 | Shielded | 30/15 PE/PVC - 7 Strand
14 | 6 |  | 0.030/0.015 | 0.060 | 0.650 | 259 | Shielded | 30/15 PE/PVC - 7 Strand
12 | 2 |  | 0.030/0.015 | 0.045 | 0.478 | 142 | Shielded | 30/15 PE/PVC - 7 Strand
10 | 2 |  | 0.030/0.015 | 0.060 | 0.570 | 201 | Shielded | 30/15 PE/PVC - 7 Strand
10 | 4 |  | 0.030/0.015 | 0.060 | 0.650 | 307 | Shielded | 30/15 PE/PVC - 7 Strand
10 | 8 |  | 0.030/0.015 | 0.080 | 0.910 | 581 | Shielded | 30/15 PE/PVC - 7 Strand
6 | 4 |  | 0.030/0.015 | 0.060 | 0.820 | 571 | Shielded | 30/15 PE/PVC - 7 Strand
8 | 2 |  | 0.045/0.015 | 0.060 | 0.655 | 272 | Shielded | 45/15 PE/PVC - 7 Strand
8 | 3 |  | 0.045/0.015 | 0.060 | 0.694 | 357 | Shielded | 45/15 PE/PVC - 7 Strand
8 | 5 |  | 0.045/0.015 | 0.080 | 0.878 | 570 | Shielded | 45/15 PE/PVC - 7 Strand
6 | 2 |  | 0.045/0.025 | 0.060 | 0.778 | 411 | Shielded | 45/25 PE/PVC - 7 Strand
6 | 3 |  | 0.045/0.025 | 0.080 | 0.870 | 563 | Shielded | 45/25 PE/PVC - 7 Strand
6 | 9 |  | 0.045/0.025 | 0.080 | 1.346 | 1374 | Shielded | 45/25 PE/PVC - 7 Strand
4 | 3 |  | 0.045/0.025 | 0.080 | 0.976 | 738 | Shielded | 45/25 PE/PVC - 7 Strand
4 | 1 |  | 0.045/0.030 | 0.045 | 0.487 | 291 | Shielded | 45/30 PE/PVC - 7 Strand
2 | 1 |  | 0.045/0.030 | 0.045 | 0.535 | 382 | Shielded | 45/30 PE/PVC - 7 Strand

## Copper conductor
Size | Stranding | Material | DIAM Inches | GMR Feet | RES Ω/mile | Amps
1 | 7_STRD | Copper | 0.328 | 0.00992 | 0.765 | 270
2 | 7_STRD | Copper | 0.292 | 0.00883 | 0.964 | 230
2 | 1_STRD | Copper | 0.258 | 0.00836 | 0.945 | 220
3 | 1_STRD | Copper | 0.229 | 0.00745 | 1.192 | 190
4 | 1_STRD | Copper | 0.204 | 0.00663 | 1.503 | 170
5 | 1_STRD | Copper | 0.1819 | 0.0059 | 1.895 | 140
6 | 1_STRD | Copper | 0.162 | 0.00526 | 2.39 | 120
7 | 1_STRD | Copper | 0.1443 | 0.00468 | 3.01 | 110
8 | 1_STRD | Copper | 0.1285 | 0.00416 | 3.8 | 90
9 | 1_STRD | Copper | 0.1144 | 0.00371 | 4.6758 | 80
10 | 1_STRD | Copper | 0.1019 | 0.00330 | 5.9026 | 75
12 | 1_STRD | Copper | 0.0808 | 0.00262 | 9.3747 | 40
14 | 1_STRD | Copper | 0.0641 | 0.00208 | 14.8722 | 20
16 | 1_STRD | Copper | 0.0508 | 0.00164 | 23.7262 | 10
18 | 1_STRD | Copper | 0.0403 | 0.00130 | 37.6726 | 5
19 | 1_STRD | Copper | 0.0359 | 0.00116 | 47.5103 | 4
20 | 1_STRD | Copper | 0.032 | 0.00103 | 59.684 | 3
22 | 1_STRD | Copper | 0.0253 | 0.00082 | 95.4835 | 2
24 | 1_STRD | Copper | 0.0201 | 0.00065 | 151.616 | 1
1/0 | 7_STRD | Copper | 0.368 | 0.01113 | 0.607 | 310
2/0 | 7_STRD | Copper | 0.414 | 0.01252 | 0.481 | 360
3/0 | 12_STRD | Copper | 0.492 | 0.01559 | 0.382 | 420
3/0 | 7_STRD | Copper | 0.464 | 0.01404 | 0.382 | 420
4/0 | 12_STRD | Copper | 0.552 | 0.0175 | 0.303 | 490
4/0 | 19_STRD | Copper | 0.528 | 0.01668 | 0.303 | 480
4/0 | 7_STRD | Copper | 0.522 | 0.01579 | 0.303 | 480
250,000 | 12_STRD | Copper | 0.6 | 0.01902 | 0.257 | 540
250,000 | 19_STRD | Copper | 0.574 | 0.01813 | 0.257 | 540
300,000 | 12_STRD | Copper | 0.657 | 0.0208 | 0.215 | 610
300,000 | 19_STRD | Copper | 0.629 | 0.01987 | 0.215 | 610
350,000 | 12_STRD | Copper | 0.71 | 0.0225 | 0.1845 | 670
350,000 | 19_STRD | Copper | 0.679 | 0.0214 | 0.1845 | 670
400,000 | 19_STRD | Copper | 0.726 | 0.0229 | 0.1619 | 730
450,000 | 19_STRD | Copper | 0.77 | 0.0243 | 0.1443 | 780
500,000 | 19_STRD | Copper | 0.811 | 0.0256 | 0.1303 | 840
500,000 | 37_STRD | Copper | 0.814 | 0.026 | 0.1303 | 840
600,000 | 37_STRD | Copper | 0.891 | 0.0285 | 0.1095 | 940
700,000 | 37_STRD | Copper | 0.963 | 0.0308 | 0.0947 | 1040